## Sheet1
Text | Discipline | created_by | created_at
Fab / Del Steel - Base | Structural | II | 2023-10-10
Install Blocking 7th Floor Roof | Structural | Final Reckoning | 2023-10-06
Ceiling Concealment Inspections | Architecture | III | 2023-10-02
Fab / Del WD-03 | no | Final Reckoning | 2023-10-02
Punch Walk w/Owner 2nd Floor | Architecture | II | 2023-10-08
Tree Removal Part 1 | Civil | Dead Reckoning | 2023-10-04
Shaft Walls First Level | Structural | Final Reckoning | 2023-10-08
Point Up & Paint (Bathroom) | Architecture | Ghost Protocol | 2023-10-10
CONSTRUCTION | no | Dead Reckoning | 2023-10-06
CONSTRUCTION | no | II | 2023-10-06
Temp Trash Chute Comeback Work (West) | no | Ghost Protocol | 2023-10-06
Set Tubs & Shower Pans First Level | Plumbing | Ghost Protocol | 2023-10-06
Fire Alarm | Fire Protection | I | 2023-10-09
Install flooring | Architecture | Rogue Nation | 2023-10-09
Core & Shell Building Inspection | Architecture | II | 2023-10-01
Cermaic Tile | Architecture | Ghost Protocol | 2023-10-07
Procurement and Fabrication | no | Ghost Protocol | 2023-10-03
Permanent Power | Electrical | Ghost Protocol | 2023-10-06
Frame/ Rough-in/ Pour Slab (Eleventh Level Pour #1) | Structural | I | 2023-10-09
Nana Wall Supports | Structural | III | 2023-10-09
Point-up / 1st Coat of Paint First Level (Corridor) | Architecture | III | 2023-10-09
Rub & Finish Concrete Stair A | Structural | Fallout | 2023-10-03
Final Inspections Elev 4 | no | Dead Reckoning | 2023-10-07
Procure Sprinkler Shop Drawings | Fire Protection | Dead Reckoning | 2023-10-05
Install Lights & Diffusers | Electrical | I | 2023-10-06
PRECONSTRUCTION | no | Fallout | 2023-10-08
AIMCO DC OFFICE | no | III | 2023-10-02
Set Tubs & Shower Pans Seventh Level | Plumbing | Dead Reckoning | 2023-10-09
A/E Review Flooring Submittals | Architecture | Dead Reckoning | 2023-10-02
Mud Set (Bathroom) | Architecture | II | 2023-10-01
DEV Wiring at Transformers | Electrical | I | 2023-10-02
Frame Gyp Ceilings | Architecture | Ghost Protocol | 2023-10-10
Owner Punchout Tenth Level (Corridor) | Architecture | Fallout | 2023-10-06
Prepare & Submit Switchgear Package | Electrical | II | 2023-10-07
Prime Coat of Paint Eighth Level (Units) | Architecture | I | 2023-10-05
ARCH Hardware & Trimout Fifth Level (Units) | Architecture | Fallout | 2023-10-02
baths/golf | no | Rogue Nation | 2023-10-10
Hang Drywall Eleventh Level (Units/Corridors) | Architecture | Rogue Nation | 2023-10-07
Plumbing | Plumbing | II | 2023-10-09
A/E Review | Architecture | Dead Reckoning | 2023-10-02
Fab / Del Mechanical | Mechanical | II | 2023-10-01
Prime and Paint | Architecture | Dead Reckoning | 2023-10-05
Plumbing Fixtures 9th | Plumbing | Rogue Nation | 2023-10-07
Exterior CMU Walls P2 Level | Structural | Rogue Nation | 2023-10-08
A/E Review Tile Submittals | Architecture | I | 2023-10-04
Flooring Demolition | Architecture | Ghost Protocol | 2023-10-08
Owner Punchout Sixth Level (Units) | Architecture | Dead Reckoning | 2023-10-09
Punch & Final Clean | Architecture | II | 2023-10-01
Partition Concealment Inspections | Architecture | Rogue Nation | 2023-10-10
Pour Slab on Grade (P2 Level Pour #5) | Structural | Ghost Protocol | 2023-10-04
Paint | Architecture | III | 2023-10-01
Prepare & Submit Metal Panel Shop Drawings | Architecture | I | 2023-10-10
Construction | no | Rogue Nation | 2023-10-03
Exterior Sheathing Ninth Level | Architecture | Final Reckoning | 2023-10-02
Cooling Tower Piping | Mechanical | Dead Reckoning | 2023-10-04
Remove Any and All Lead Painted Plaster | Architecture | I | 2023-10-07
Hang Drywall Eighth Level (Units/Corridors) | Architecture | Ghost Protocol | 2023-10-08
Prime Coat of Paint Eleventh Level (Corridor) | Architecture | Fallout | 2023-10-09
Sprinkler Heads Modifications | Fire Protection | III | 2023-10-02
Finish Drywall Fifth Level (Units) | Architecture | Final Reckoning | 2023-10-06
Wall Layout and HM Frames First Level | Architecture | Rogue Nation | 2023-10-09
MoCo Review FA SD | Fire Protection | III | 2023-10-10
Plumbing Fixtures 4th | Plumbing | II | 2023-10-04
Prime Coat of Paint Second Level (Units) | Architecture | Fallout | 2023-10-09
Test Gas Piping | Plumbing | III | 2023-10-02
Clean Garage P2 Level | Architecture | II | 2023-10-05
Glass/Mirrors - Base | Architecture | Final Reckoning | 2023-10-06
Sprinkler System | Fire Protection | III | 2023-10-01
DCC Punch Facade (East Courtyard) | Architecture | II | 2023-10-06
Paint Final Paint | Architecture | Final Reckoning | 2023-10-02
Saw Cut & Remove SOG | Structural | Final Reckoning | 2023-10-05
Air Barrier Pre-wrap for Windows Seventh Level | Architecture | Ghost Protocol | 2023-10-08
Excavate to Tieback Elevation 3rd Row (beams 24-37) | Civil | Final Reckoning | 2023-10-07
Patch Tower Crane Slab Opening (P2 Level) | Structural | Dead Reckoning | 2023-10-04
DCC Site Punch Transformer Yard | Electrical | Dead Reckoning | 2023-10-06
Procure Light Fixtures | Electrical | II | 2023-10-05
Acoustical Panels | Architecture | Ghost Protocol | 2023-10-05
Final Point-up / Final Coat of Paint Third Level (Units) | Architecture | I | 2023-10-07
Prime / 1st Coat of Paint Walls & Soffits | Architecture | II | 2023-10-06
Hang & Finish Walls | Architecture | Final Reckoning | 2023-10-06
Fab & Deliver Boilers | Mechanical | III | 2023-10-09
DEV Set Apartment Meters Floors 9 thru 12 | Electrical | Dead Reckoning | 2023-10-04
DEV Set Apartment Meters Floors 5 thru 8 | Electrical | Ghost Protocol | 2023-10-05
Excavate & Berm (beams 38-57) | Civil | III | 2023-10-01
Frame/ Rough-in/ Pour Slab (First Level Pour #2 ) | Structural | Final Reckoning | 2023-10-05
Finish Drywall Second Level (Units) | Architecture | Final Reckoning | 2023-10-10
Plantings | Landscape Architecture | Rogue Nation | 2023-10-04
Install Roof Soil 11th Floor Roof | Landscape Architecture | III | 2023-10-09
East Courtyard Facade | Architecture | Fallout | 2023-10-01
Prepare & Submit Tile Samples | Architecture | Rogue Nation | 2023-10-10
Corridors Light Fixtures | Electrical | Dead Reckoning | 2023-10-08
Construction 16th Floor | no | III | 2023-10-09
DCC Punch Facade (North Courtyard) | Architecture | I | 2023-10-10
DCC Punchout Ninth Level (Corridor) | Architecture | Ghost Protocol | 2023-10-02
Frame/ Rough-in/ Pour Slab (Seventh Level Pour #3) | Structural | III | 2023-10-02
Paint | Architecture | Ghost Protocol | 2023-10-08
Procure Electrical Panels | Electrical | Fallout | 2023-10-04
Prepare & Submit Storefront Shop Drawings | Architecture | II | 2023-10-06
Appliances Fifth Level (Units) | Interior Design | Dead Reckoning | 2023-10-01
Adjustments for Temp Use Inspection Elev 4 | no | Ghost Protocol | 2023-10-04
Prime Coat of Paint Ninth Level (Corridor) | Architecture | Final Reckoning | 2023-10-07
Install TURF | Landscape Architecture | Final Reckoning | 2023-10-07
Reconfigure Temp Protection | no | Fallout | 2023-10-03
Hang/Finish Drywall Partitions | Architecture | Fallout | 2023-10-05
Mech. Trimout 5th | Mechanical | Rogue Nation | 2023-10-07
Exterior Stud Walls Second Level | Structural | Final Reckoning | 2023-10-02
Paint Partitions | Architecture | II | 2023-10-07
Revised Bar Plumbing Drawings Issued | Plumbing | Final Reckoning | 2023-10-04
Hang Doors | Architecture | Ghost Protocol | 2023-10-09
Set Tubs & Shower Pans Ninth Level | Plumbing | Final Reckoning | 2023-10-01
A/E Review NanaWall Submittal | Architecture | III | 2023-10-05
DECK POUR #1 | Structural | Fallout | 2023-10-03
Dock Seals | Architecture | II | 2023-10-09
Prime & 1st Coat | Architecture | Final Reckoning | 2023-10-09
Shutdown 7-US3 | no | Rogue Nation | 2023-10-03
Terminate TELE Devices @ Mechanical E114 - Unit F1 | Communications | Fallout | 2023-10-05
Install Domestic CW @ Circulation A004 - Unit A1 | Plumbing | III | 2023-10-07
Roof Metal Decking - Seq 13 Unit A1 | Structural | Dead Reckoning | 2023-10-08
South Exterior Replacement - Install Light Fixtures | Electrical | Rogue Nation | 2023-10-04
VAV/Low pressure Duct | Mechanical | I | 2023-10-09
Ceiling Tile | Architecture | II | 2023-10-07
L2-MR Corridor - Blocking Installation | Architecture | Fallout | 2023-10-08
ED L2 Area 26 - Out of Sequence Heating Hot Water Overhead | Mechanical | Ghost Protocol | 2023-10-07
LG&E Undeground Gas Service | Civil | I | 2023-10-02
Dock Grading & Paving - xfmr to SW ramp | Civil | Ghost Protocol | 2023-10-05
Test Domestic & SCW (Existing CUP) | Plumbing | II | 2023-10-04
Erect - Detal Balance of Structural Steel connecting and around the Lab Building | Structural | I | 2023-10-01
Install Ductwork Post Priority - Unit D2 | Mechanical | I | 2023-10-10
Firestop Above Ceiling Prior to Grid | Fire Protection | Final Reckoning | 2023-10-08
Stryker SK Boxes Delivered | no | I | 2023-10-09
HW / CW Pumps - Submittals Review / Approve | Mechanical | Final Reckoning | 2023-10-04
Install UG Waterline (Tee to Ball Diamond Hydrant) | Civil | Fallout | 2023-10-09
SI L3 Area 10 - Deliver Air Devices | Mechanical | III | 2023-10-09
ED G Area 15 - Electric Conduit Mains | Electrical | Final Reckoning | 2023-10-05
SI L2 Area 7 - TDR Dress Copper | Communications | Rogue Nation | 2023-10-01
Storm Install | Civil | I | 2023-10-01
In Grid Electrical R/I @ B1 | Electrical | Dead Reckoning | 2023-10-10
Wall Punchlist | Architecture | III | 2023-10-02
Final Paint @ B1 - Mech Rm East | Architecture | Final Reckoning | 2023-10-05
Install Door Operator (1PM Install?) | Architecture | Dead Reckoning | 2023-10-02
Sheet Metal Submittal Review (Poynter) | Mechanical | II | 2023-10-03
ED G Area 15 - Fire Alarm Devices Programming | Fire Protection | Fallout | 2023-10-10
3M Commissioining of Draw System 1 | Mechanical | III | 2023-10-07
Remove Temp School Stone @ Perimeter | Civil | Dead Reckoning | 2023-10-03
Ceiling Tile @ Area C1 - Stair #5 | Architecture | III | 2023-10-07
A - Finish Drywall | Architecture | Final Reckoning | 2023-10-01
Install AV, Speakers & Cameras in Ceiling | Communications | Final Reckoning | 2023-10-03
Startup - AHU8 @ B4 - Mech Rm East | Mechanical | Fallout | 2023-10-06
SI G Area B - Sanitary and Storm Risers | Plumbing | Ghost Protocol | 2023-10-01
Final Electrical Connections and Trim | Electrical | III | 2023-10-01
A - Prime/First Coat | Architecture | II | 2023-10-01
SI L2 Area 9 - Nurse Call J-Hook Installation | Communications | III | 2023-10-02
A/B - Aggregate Piers | Structural | III | 2023-10-05
Terminate FA Devices @ Staff/Resource & Restroom - Unit B1 | Fire Protection | II | 2023-10-03
Mont Reid Elevator Lobby - Prime and 1st Coat | Architecture | III | 2023-10-07
SPD Phase 4 Flooring Prep & Floor Install (Night Shift) | Architecture | Ghost Protocol | 2023-10-07
Top Out Walls | Structural | Final Reckoning | 2023-10-01
Install Power and Pathway at New Screen & Connectrac | Electrical | II | 2023-10-07
Basement Wall Backfill First Lift (West Half) | Civil | Ghost Protocol | 2023-10-04
Hydronic Piping & Testing @ B2 | Mechanical | Final Reckoning | 2023-10-01
Quality Review L6 Slab Depression | Structural | Final Reckoning | 2023-10-04
Casework | Interior Design | Final Reckoning | 2023-10-10
ED L2 Area 26 - Duct Mains (High Pressure) Hang | Mechanical | Dead Reckoning | 2023-10-01
ED L1 Area 16 - Fire Caulk - Final Pass & Wall Labeling | Fire Protection | Final Reckoning | 2023-10-05
ED L1 Area 18 - Duct Mains (High Pressure) Hang | Mechanical | Ghost Protocol | 2023-10-10
SI 1 Elevator Misc Steel Supports (Elevators 10, 11 & 12) | Structural | II | 2023-10-01
Ceiling Grid | Architecture | Ghost Protocol | 2023-10-02
MP3 Punch Window Install North Elevation (15 ea #26's) | Architecture | Final Reckoning | 2023-10-05
Install Wood Doors | Architecture | II | 2023-10-07
CLT Water Plan Approval - British School Playfield | Civil | Fallout | 2023-10-07
Lead Time - AHU 4 | Mechanical | III | 2023-10-09
EDR G Non-Flow - G591 - Install Base | Architecture | I | 2023-10-06
ED L1 Area 18 - Acoustical Ceiling Border Pad Install | Architecture | I | 2023-10-05
Wall Protection (Only Trade In Room) | Architecture | II | 2023-10-05
EDR G Area 30 - Security Wire Pull | Communications | Final Reckoning | 2023-10-03
Custom AHUs Lead Time | Mechanical | Fallout | 2023-10-09
ED Exterior Wall Assembly Prep Meeting | Architecture | Dead Reckoning | 2023-10-07
Medium Pressure Duct @ A4 | Mechanical | II | 2023-10-10
SI 2 Stair - Prime & 1st Coat | Architecture | Ghost Protocol | 2023-10-02
Feeder from 001P-109 fro IUS3 | Electrical | Rogue Nation | 2023-10-02
Metal Stud Framing Repairs (Walls) | Structural | II | 2023-10-05
SI L2 Area 9 - Finish Drywall (outside OR's) | Architecture | Final Reckoning | 2023-10-03
AVI Installation | Communications | III | 2023-10-09
Touch Up Walls | Architecture | Ghost Protocol | 2023-10-06
AVI Installation | Communications | II | 2023-10-01
Field Measure - Duct Mech 210 | Mechanical | Final Reckoning | 2023-10-09
ED L1 Area 19 - Wall Protection Delivery | Architecture | Fallout | 2023-10-04
Steel Topping Out (Review Top Out Procedure with NCH) | Structural | I | 2023-10-04
SPD Phase 2 Duct Insulation | Mechanical | Ghost Protocol | 2023-10-04
Install Flooring | Architecture | II | 2023-10-10
ED L2 - Install Switches and Connect to Patch Panels (TDR 2655) | Communications | III | 2023-10-04
Frame Walls | Structural | Final Reckoning | 2023-10-04
Remove Wall Mounted Items to be Salvaged | Architecture | Rogue Nation | 2023-10-10
Structural Steel Sequence 7 & 8 Approval | Structural | I | 2023-10-04
VAV/Low pressure Duct | Mechanical | I | 2023-10-08
Wall Rails | Architecture | I | 2023-10-03
Mechanical Piping/Insulation Overhead - - Extrusion/Draw | Mechanical | II | 2023-10-10
Air Curtains Install & Final Connections | Mechanical | Fallout | 2023-10-08
Cut-in FP Heads @ Corridor C004 - Unit C1 | Fire Protection | III | 2023-10-03
SI-1 Area A - Fire Protection Sleeves | Fire Protection | Ghost Protocol | 2023-10-05
Final Paint @ A3 | Architecture | Final Reckoning | 2023-10-05
Mech Piping R/I & Testing @ A2 | Mechanical | III | 2023-10-05
L2-PACU - Above Ceiling Electrical Inspection - Phase 1 (East Door) | Electrical | III | 2023-10-05
Acclimate Wood Flooring @ D (Main Gym) | Architecture | Final Reckoning | 2023-10-08
ED 3 Area 25 - Fire Caulk | Fire Protection | Final Reckoning | 2023-10-10
SPD Phase 4 Electric In-Wall Inspection | Electrical | Fallout | 2023-10-09
Med Gas Control Wiring | Electrical | Fallout | 2023-10-04
South Canopy Metal Roofing & Flat Roof | Architecture | Final Reckoning | 2023-10-04
Install Plywood on the Backside of Precast for Roofing | Structural | Rogue Nation | 2023-10-03
SE Rammed Aggregate Piers | Structural | Dead Reckoning | 2023-10-08
SI 2 Stair - Hang Drywall walls and soffits (Green Board) | Architecture | Ghost Protocol | 2023-10-05
Mount TELE Devices @ Corridor B020 - Unit B2 | Communications | Ghost Protocol | 2023-10-08
BP # 7 Mont Reid Scaffolding | Structural | Ghost Protocol | 2023-10-04
Wall Framing / Priority Wall Topout @ B1 | Structural | II | 2023-10-02
SER Hang and Finish Walls LB6744 | Architecture | I | 2023-10-07
Install Ceiling Grid @ Cafe F100 - Unit F1 | Architecture | Final Reckoning | 2023-10-03
SI G Area 2 - Storm/Sanitary/Vent Mains Hang | Plumbing | II | 2023-10-01
Prep and Pourback Concrete Slabs at Plumbing | Structural | II | 2023-10-01
ED-Roof - Roof AVB Level 1 | Architecture | I | 2023-10-01
Install Ceiling Grid @ Opportunity Rm E100 - Unit E1 | Architecture | Rogue Nation | 2023-10-01
Install Ductwork @ Athletic Locker Room G102-103 - Unit G1 | Mechanical | Fallout | 2023-10-06
SI 2 Stair #3- Conduit In Wall Rough-In | Electrical | Dead Reckoning | 2023-10-05
Install Pac Box (2) | Electrical | Fallout | 2023-10-06
ED L2 Area 20 - Security Devices | Communications | II | 2023-10-09
Irrigation @ Softball | Landscape Architecture | Ghost Protocol | 2023-10-08
EDR G Area 27 - Duct Branch (Low Pressure) - Inspection | Mechanical | III | 2023-10-01
ED REN Phase 1 - Data Wire Pull | Communications | Final Reckoning | 2023-10-06
Drop Ceiling Tiles | Architecture | III | 2023-10-04
Trim Out Equipment (AHU-1) | Mechanical | Fallout | 2023-10-04
Central Lab Radius Brick Removal for steel connections | Structural | Dead Reckoning | 2023-10-03
In-Wall Blocking | Structural | I | 2023-10-09
Terminate BMS Devices @ Staff/Resource & Restroom - Unit B1 | Communications | Rogue Nation | 2023-10-03
Electrical In Wall Rough In & Low Voltage Rough In | Electrical | Rogue Nation | 2023-10-05
Prime & 1st Coat Paint @ A2 | Architecture | Ghost Protocol | 2023-10-04
Area S4 | no | Ghost Protocol | 2023-10-08
Med Gas Control Wiring | Electrical | II | 2023-10-08
SPD Phase 2 Plumbing Inwall Installation, Inspection and Insulate | Plumbing | Rogue Nation | 2023-10-02
Frame Soffits | Architecture | Ghost Protocol | 2023-10-10
Basement Wall Waterproofing 2nd lift (East Half) | Structural | Dead Reckoning | 2023-10-02
SPD Phase 4 Insulation - VAV(s) Feeding Dirty Side | Mechanical | II | 2023-10-07
ED L2 Area 26 - Above Ceiling Duct Inspections | Mechanical | Rogue Nation | 2023-10-03
Wall Crew North Pour 2-9 | Structural | III | 2023-10-05
Final Drywall Touch Up Stairs | Architecture | Rogue Nation | 2023-10-07
Form & Pour - West Parking Lot Curb & Gutter - S | Civil | Dead Reckoning | 2023-10-01
ED L2 Area 21 - Plumbing Branch Pipe Insulation | Plumbing | I | 2023-10-06
09 51 13 Acoustical Panel Ceilings (A/E Review) | Architecture | Rogue Nation | 2023-10-01
Ph. 2 - Concrete Pavement (Area #2) - Prep for Pour | Civil | III | 2023-10-02
EDR G Area 29 - Install Valve Tags (Soffits & Hard Ceilings) | Mechanical | II | 2023-10-03
Frame Ceilings | Architecture | Ghost Protocol | 2023-10-02
Mount BMS Devices @ Rms E103-105-1010 - Unit E1 | Communications | II | 2023-10-01
ED L1 Area 16 - Air Devices Lead Time | Mechanical | III | 2023-10-05
HHW / CW Branches | Mechanical | III | 2023-10-05
Mechanical Final | Mechanical | I | 2023-10-06
DWV/Storm Install | Plumbing | Ghost Protocol | 2023-10-05
L2 Curtain Wall Layout | Architecture | Fallout | 2023-10-03
Ceramic Tile - Fabrication | Architecture | Final Reckoning | 2023-10-04
Garden Punchlist | Landscape Architecture | Final Reckoning | 2023-10-08
Rough Grade Main Drive | Civil | Ghost Protocol | 2023-10-07
ED-South-East Third Terracotta Panel Installaiton | Architecture | Fallout | 2023-10-10
Design - 95% Bid Set - Issued | Architecture | III | 2023-10-10
Renovation - A/E Punchlist - West | Architecture | III | 2023-10-08
Install Storm (MH-6 to MH-8) | Civil | I | 2023-10-03
Tower Building Envelope and Shafts | Architecture | Fallout | 2023-10-04
Swing HM Doors | Architecture | III | 2023-10-04
EDR G Area 29 - Frame Remaining Walls and soffits | Structural | Fallout | 2023-10-07
SOG Prep and Pour 1 | Structural | II | 2023-10-05
SI L2 Area 8 - Drywall Sprinkler Escutcheon Plate Installation | Fire Protection | Ghost Protocol | 2023-10-01
ED G Area 13 - Drywall soffit/ceiling Sprinkler Head Drops | Fire Protection | Final Reckoning | 2023-10-02
Chilled Water VFD Release | Mechanical | Fallout | 2023-10-10
Top Out Walls | Structural | Final Reckoning | 2023-10-08
ED G Area 15 - Pneumatic Transfer Stations | Mechanical | Fallout | 2023-10-09
Install FA Rough-in @ Staff/Resource & Restroom - Unit C1 | Fire Protection | I | 2023-10-07
ED L1 Area 19 - Interior Aluminum Door and Glass Installation | Architecture | II | 2023-10-03
Demo Walls, Ceilings, and Flooring | Architecture | I | 2023-10-03
ED Pour 9A Concrete Cure time | Structural | Fallout | 2023-10-04
Homerun Conduit | Electrical | Fallout | 2023-10-01
SI Level 3 Water Balancing | Mechanical | Fallout | 2023-10-03
Foundations | Structural | Fallout | 2023-10-10
ED L1 Area 16 - Fire Caulk - Storm/Sanitary/Vent/Water/Med Gas Branch | Fire Protection | Ghost Protocol | 2023-10-10
Playing Field Storm Underdrain | Civil | Rogue Nation | 2023-10-03
ED Pour 9C Perimeter/Edge Forms | Structural | Fallout | 2023-10-07
Final Clean | Architecture | I | 2023-10-05
A/B - Poduim Slab Decking (Pour Two) | Structural | Ghost Protocol | 2023-10-06
Hang Gypsum @ Class Rms C100-106 - Unit C1 | Architecture | II | 2023-10-10
ED REN Area 28 - Fabricate Duct Branch (Low Pressure) | Mechanical | Ghost Protocol | 2023-10-01
ED-G-SE Stair #1 - Conduit In-Wall Inspection | Electrical | Rogue Nation | 2023-10-10
ED REN Phase 1 - Construction Clean | Architecture | Final Reckoning | 2023-10-01
Continuous Footing - Unit E | Structural | Fallout | 2023-10-02
Frame & Hang Sliding Door 175 | Architecture | I | 2023-10-01
SI G Stair - Finish Drywall | Architecture | I | 2023-10-08
MILESTONE: Power onto Electrical Panels in Knitting (9/1) | Electrical | III | 2023-10-09
EDR G Area 29 - Layout Fire Suppression Heads (Soffits & Hard Ceilings) | Fire Protection | Ghost Protocol | 2023-10-02
ED-West-2 - Curtain Wall - 43 (Garden N) | Architecture | Rogue Nation | 2023-10-08
Floor Protection | Architecture | Final Reckoning | 2023-10-03
26 05 19 Low Voltage Electrical Power Conductors And Cables (A/E Review) | Electrical | Ghost Protocol | 2023-10-03
SI L2 OR's - Shop Drawings Prefabed Air Frame - Steel Design | Structural | Dead Reckoning | 2023-10-05
BP #7 - Areas 8 - Revised Steel Shop Drawing Approval Process | Structural | Ghost Protocol | 2023-10-03
Prime & Paint Second Coat @ Main Gym G100 - Unit G1 | Architecture | Rogue Nation | 2023-10-08
Temp Field Stabilization | Civil | Fallout | 2023-10-07
SI G Area 4 - Deliver Duct Branch (Low Pressure) | Mechanical | Dead Reckoning | 2023-10-03
SI G Area 4 - Ceiling Replacement due to Stainless Duct Replacement | Architecture | III | 2023-10-03
Imaging Phase 6 (Staff Toilet) | Architecture | Rogue Nation | 2023-10-04
Central Lab & CCP Ground floor EMS Lounge & PAT Bay 4 - Mechanical Research | Mechanical | Rogue Nation | 2023-10-07
Flooring Type 2 | Architecture | Final Reckoning | 2023-10-07
Install TELE Rough-in @ Platform F102 - Unit F1 | Communications | Final Reckoning | 2023-10-03
CONCRETE CURB FOR GREEN ROOF DETAIL CLARIFICATION There seems to be a difference in construction methods between the Details on A44.2.4 & A426.4. Please clarify which how these details. | Architecture | Dead Reckoning | 2023-10-04
Stairpress Wall Supply Register Elevation Confirmation As discussed via email, please confirm the bottom of the stair pressurization wall supply register shall be at least 6'-0" above the stairwell landing (if the duct tap & register do not protrude more than 4" from the face of the wall). | Mechanical | II | 2023-10-05
Bldg 2 Gap at Stair Shaft Thresholds Reference is made to attached image. There is a 1/2" to 3/4" gap between the stair shaft slab and corridor door threshold at all stair shaft door locations. Per Mike Hale this gap needs to be covered. One solution would be to install a larger threshold at the stair shaft doors. Please advise how you would like us to proceed. | Architecture | Ghost Protocol | 2023-10-03
1st Floor Slab Edge Plan Please reference sheet A102_S. There are 2 different edge of slab elevations given near gridline 4 (58.2' vs 58.55'). Please clarify where the 4" step down occurs on plan. See M&L RFI #143 attached in references. | Architecture | III | 2023-10-06
1st Floor Slab Edge Plan Please reference sheet A102_S. There are 2 different edge of slab elevations given near gridline 4 (58.2' vs 58.55'). Please clarify where the 4" step down occurs on plan. See M&L RFI #143 attached in references. | Architecture | Dead Reckoning | 2023-10-10
BIM RFI - Conflict in E002 with vent space PerÂ 5/10/22Â BIMÂ meeting:Â WeÂ eitherÂ needÂ toÂ coreÂ higher,Â moveÂ thisÂ ventÂ toÂ theÂ higherÂ NorthÂ roof,Â orÂ implementÂ aÂ mechanical ventÂ inÂ E002.Â WeÂ doÂ notÂ haveÂ enoughÂ spaceÂ toÂ getÂ theÂ ventÂ upÂ aroundÂ thisÂ ductÂ currentlyÂ (blueÂ lineÂ cuttingÂ south).Â Â Please confirmÂ anÂ acceptableÂ solution.Â Â AttachedÂ isÂ snapÂ ofÂ areaÂ forÂ reference. | Mechanical | II | 2023-10-01
Building G - Column A6 Foundation Wall Clarifications See attached. Clarification needed for wall line at the corner of Building G, West Pad, Southeast Corner. Area highlighted in red is the assumed wall line. | Architecture | Fallout | 2023-10-04
Bldg 2 Fire Smoke Dampers/ Smoke Detectors at Stair Press Shaft and Stairwell Reference is made to Bldg 2 M1.01, M4.00, E1.01, and the attached inspection report. Following the inspection of the stair pressurization system, the fire protection engineer provided a list of deficiencies on his inspection report pertaining to the installation of the stair pressurization system and the smoke detectors/ fire smoke dampers that service it. Please note that the items called out on his list were installed per approved plans. Please see the called out deficiencies below: 1. Smoke detectors for the control of stair press must be located corridor side of stair door, not in stair shaft. 2. Stair press shaft should not have fire/smoke dampers that will prevent operation of the stair press when smoke is present. Please advise how we are to proceed. | Fire Protection | II | 2023-10-02
CFMF Header Support at Elevator Entrances Per comment on returned submittal 142100-002-0, please advise if & where structural steel is required for CFMF headers at elevator entrances. | Structural | Final Reckoning | 2023-10-01
Bldg 1 Elevator Sump Pits Reference is made to sheet B1 P1.00. Neither the architectural nor the structural drawings call for a sump pit at the Building 1 elevators. We currently have space for a 24â€™x24â€x18â€D sump pit at these locations which will allow for a 3â€ cover over the lower rebar. Please confirm this is acceptable structurally and is acceptable for the volume going into these pits. | Structural | I | 2023-10-09
Lintel Type required at F104.1 The response to this RFI stating this opening was changed to an L1 during the shop drawing review for this steel sequence. This change was not reflected on the architectural or any other drawings in the construction documents. Due to this, a Prescriptive Block Lintel was installed per the structural requirements. The RFI response provided a solution to install a steel plate and utilize the existing condition or remove and install an L1 lintel beam to complete the opening system. Please advise on which method is required. | Structural | I | 2023-10-08
Duct Sizes for TE-02 Risers Clarification Reference attached and sheet M4.02: Duct Sizes for TE-02 are missing from riser diagram M4.02. Please provide duct sizes and revise riser diagram accordingly. | Mechanical | II | 2023-10-03
Duct Sizes for TE-02 Risers Clarification Reference attached and sheet M4.02: Duct Sizes for TE-02 are missing from riser diagram M4.02. Please provide duct sizes and revise riser diagram accordingly. | Mechanical | I | 2023-10-04
Level 2 & 3 Open Questions See Attached for Documentation Purposes. | no | Rogue Nation | 2023-10-01
Air Device Layout with Joists Please see attached mark-up indicating the location of the joists in blue. Note that some of the joists do not go all the way to the exterior wall, leaving room for diffusers in those locations. As discussed on-site, the supply diffusers have a plenum that barely fits in between the joists, so the layout of these supply diffusers needs to be adjusted based on the joist layout. Please indicate where the air devices are to be located. | Mechanical | Fallout | 2023-10-07
Switching not listed on EL1G2 in Gym CanÂ youÂ pleaseÂ provideÂ clarificationÂ onÂ whatÂ theÂ switchingÂ needsÂ toÂ beÂ inÂ theÂ GymÂ (G100)?Â SomeÂ ofÂ theÂ fixturesÂ notedÂ on drawingÂ EL1G2Â haveÂ aÂ "?"Â shown. | Electrical | Ghost Protocol | 2023-10-06
Unit A3 (Tier x05) Dimensions Discrepancy There is a discrepancy between dimensions on sheet A403W and detail 1 on A601 for bathroom type 1A in unit A3 (Tier x05). Sheet A403W calls for 8'-11 1/2" while detail 1/A601 calls for 9'-0". Please confirm 8'-11 1/2" dimension is acceptable. | Architecture | III | 2023-10-08
CMU abutting walls alternate reinforcement request Regarding areas E,F,G, and H. Where adjacent cells have mesh ties but cells are un-grouted, is it acceptable to use top of wall clip angle steel that can be added to the inside of corners where it can be welded to the steel structure. If attachment to the steel is not acceptable or applicable, DPM proposes to install angle iron steel clips on both sides of the intersecting walls above ceiling level with expansion bolts (see attachments). | Structural | Final Reckoning | 2023-10-03
Duplex Receptacles Drawing E-100 shows an Electrical Symbol (Legend) with Wall Mounted (Standard) Duplex Receptacles. Drawing AI-101 shows a Power & Signal Legend with a Duplex Receptacle w/ USB Outlets. Which should the electrician proceed with installing once the walls have been finished? | Electrical | Rogue Nation | 2023-10-08
Lighting Control Transfer Device Intent E1.01A & B Rooms with an EM lighting with no GTD called out for lights to come on in the event of a power outage. Fire pump 1007, Mechanical 1008, Corridor 1001, Electrical room 1009, Elevator Machine room 1013, Exercise Phys Lab 1004, Vestibule 1000, Exterior lighting through LCE has no control for power outage to turn lights on. This will be the same for 2nd floor and 4th floor exterior lighting. Entry C1003, Mechanical 1022, Commons C1004A, B & C. | Electrical | Final Reckoning | 2023-10-09
S. WING T&B / FCU SUPPLY AIR The S. Wing T&B report indicated 4 FCU's are low on supply and RA: S-FCU-208, S-FCU-210, S-FCU-308, S-FCU-310. Our sheet metal manager checked the connected duct systems and the FCU's for blockage, obstruction, and collapsed duct which were not found. I ask that the T&B contractor re-visit and record the SA static pressure for these units, results are attached. It appears that S-FCU-308 and S-FCU-310 have fan motor issues. S-FCU-208 and S-FCU-210 are operating within the SP range. The results of the test are attached. Please provide direction to resolve the connected load air flow issues associated with S-FCU-208 and S-FCU-210. | Mechanical | I | 2023-10-10
1st Floor Exterior Wall Outlets Wiring At exterior wall outlets on the 1st floor, the 3rd Party Inspector stated we need to protect the wire coming down the wall with metal tubing. DCC recommends switching to EMT conduit at 1st Floor exterior walls. Please confirm this is acceptable. | Electrical | Dead Reckoning | 2023-10-05
Edge of Slab Verification On 2nd floor, 3rd floor and 4 th floor area A the edge of slab differs from floor to floor; at line line 12 between C and D; are not the same at all 3 floors. Line C between line 13 and 14 the edge of slab is not the same at all 3 floors. Please Reference attachment and verify/Confirm dimensions required, see attached S1211. | Structural | Ghost Protocol | 2023-10-05
Shaft Wall in Changing Room G639A See attached overlay of structural and architectural drawing in Changing Room G639A as well as a picture from the field. The yellow highlighted wall will not hit structure above. Should we install a rated ceiling over to the shaft wall to close off this opening? | Architecture | Final Reckoning | 2023-10-01
Condensate Lines on 1st Floor Existing condensate lines on the first floor are not insulated. Please advise if donohoe should insulate these lines or leave as is. | Mechanical | Final Reckoning | 2023-10-07
Level 9 SW & Columns Low Breaks Refer to the attached 28-day break reports for Level 9 shearwalls SW-1, SW-X1, SW-X2, SW-Y2 to SW-Y5 and columns 108, 112 and 113. Cylinder Sets 01-30960-B-106 representing concrete polaced on 4/6/2023 during the Level 9 Columns and Shear Walls pour have broken below the 28-day concrete mix design strength. 01-30960-B-106-4, 5 and 6 achieved 97% of 8,000psi Design Strength. Please review the concrete strength and advise if acceptable. | Structural | Dead Reckoning | 2023-10-08
Food Service Equipment Power Requirement and Panel Designations Reference sheets E5.21, E5.22, E5.23, E7.02, E7..03, E7.05, E7.08, returned submittals 110000-005-1 and 110000-006-1: See attached PDI RFI 49 and spread sheet. Please advise and update drawings/panel schedules according to approved food service submittals. | Electrical | Ghost Protocol | 2023-10-03
Knox Box Location Please confirm the location for the Knox Box key box which provides the fire department access to the property. Reference the attached Knox Box product data and installation instructions. If it is to be located on the address side of the building, please provide a dimensioned location for where it is to be mounted. | Fire Protection | II | 2023-10-09
Stair 1 Standpipe There is a standpipe sleeve location issue on floors 11-15 in Stair #1. The sleeve is located in the middle of the South wall of the stairwell and will not be able to be used on these floors. Chipping/coring is not an option here due to PT cable group 45, which sweeps right through the south stair landing. DCC suggests routing the standpipe through the stair press shaft at the North side of the stairwell from floors 11-15 and running pipe out of the shaft at each of these affected floors with the 2" valve routing up to the south landing. Please confirm this is acceptable or advise how to proceed. | Fire Protection | II | 2023-10-06
South Patio - Gate Fencing & Security Concerns In Bulletin #15 changes there was mesh that was specified to be installed at the gates but not the adjacent fence panels. UC has concerns with their students reaching around the fencing and opening the gates to the patio area. Please advise which panels to add security mesh to? Also at the South West fence gate there is an opening between the building and the fence post. How would you like this closed off? | Architecture | Rogue Nation | 2023-10-03
HHW Piping sizes/conflicts/accessories 1. Currently at the south end of the building there are (2) 3/4" circuit setters. Please confirm if these are needed and if they should be changed out to 1" circuit setters to match pipe sizing or if another size is appropriate for system flow control. 2. Height/location of existing piping at the east end of the building is in conflict with the new ductwork and drops to diffusers. Please confirm if we can shift the HWS and HWR mains in the area shown to the east or raise them as needed to accommodate the new ductwork, or if the duct/diffusers should be shifted to the west to miss the piping mains. 3. The existing 2" HWR main crossing the corridor is to low for the new ceiling height where it crosses under the duct main. Please confirm if we are to raise the piping or lower the ceiling to accommodate. 4. The actual existing pipe sizing differs from what is shown where clouded and is 1-1/2" rather than 1-1/4". Please confirm this sizing is acceptable to stay with design flows or if it needs changed to 1-1/4". 5. Confirm the new 1-1/4" HWS piping marked on the drawing is still acceptable to be that size even through existing was 1-1/2". 6. There are (4) existing HHW valves on the main piping. Please confirm if we should replace the valves as part of the project or leave the existing valves in place. Please show valves on next sheet update. 7. Confirm if Finned Tube heaters need new control valves and tied into CCS or if they are to have a local controller. Also confirm existing unit heater on local thermostat is acceptable or if it needs to be tied into CCS. | Mechanical | Rogue Nation | 2023-10-05
Fire Pump Conductor Rating NEC 2017 Article 695.6 requires that fire pump supply conductors routed through a building shall be protected from fire for 2 hours by either encasing in concrete or using a listed fire-resistive cable system or raceway. County inspections department has stated the cabling should be rated from the GENSET to the fire pump. The cabling and pathways in the electrical room, fire pump room, and generator room meet this requirement by the nature of their location and room ratings. However, there are feeders that span the width of the corridor that must be addressed. Please see the oneline diagram attachment for more information. | Electrical | Ghost Protocol | 2023-10-10
Marker Boards on Partition Panels Sent on behalf of Minder Corp: Folding partition doors calls for full height marker boards and STC rating of 54. In lieu of full height boards, can inset marker boards be installed and reduce the STC rating to 52 in lieu of 54 to keep original pricing? See proposed drawing attached. | Architecture | II | 2023-10-02
Mounting and locations for Fixture Type 'RF02' in G2 Retail Locker Rooms The RFI response references fixture type â€˜SF19â€™. PDI did not have an â€˜SF19â€™ in the latest approved amenity submittal package - 265100-028-0 - Architectural Lighting - Amenity Fixtures Final - For Record - APPROVED.pdf. The closest fixture they have within the submittal is the â€˜SF11â€™, but the channel is different. | Electrical | Rogue Nation | 2023-10-09
EAST "Egg" Canopy panel layout confirmation Attached pdf captures design review information for the EAST Garage Entry (ref. A684) and Residential Lobby Entry â€œEggâ€ (ref A681) canopies. Info for Garage entry canopy is confirmed and install in progress. â€œEggâ€ canopy will start shortly. Katchmark requested confirmation of panel pattern layout as noted on attached, page 2 of 2. | Architecture | Ghost Protocol | 2023-10-08
Window Shade switch locations Please confirm the attached shows the correct switch grouping and switch locations for the window shades. Also please provide revised electrical drawings reflecting this information. | Electrical | II | 2023-10-07
Levels 4-8 MEP Overhead Follow ups Reference attached: Please confirm duct insulation may be removed at the (5) locations shown in RFI for Levels 4-8. | Mechanical | Final Reckoning | 2023-10-07
Plumbing Line Demo Question Plumbing drawings are showing demo of existing water, vent, and drain lines back to the riser/source. Some new plumbing work does not require full demo of these lines. Is DCC able to reuse some of the existing plumbing for new work and not demo fully to the riser/source? DCC believes if not all the existing lines have to be demoed back to the source, this will decrease the amount of work that has to be done in occupied spaces on the floor below. | Plumbing | Final Reckoning | 2023-10-02
Air Handler Unit Concrete Pad See attached. As discussed on site, this will be the location of the new air handler pad. Please confirm. | Mechanical | Ghost Protocol | 2023-10-07
Towel Bar Elevation Refer to 4/A600, A601, A602 Detail 4/A600 for the typical bathroom mounting heights for accessible and non-accessible units bathroom towel bars are to be installed 3'-6" off of finish floor. The unit bathroom elevations appear to locate the B13 towel bars at around 48" off of finish floor. Please confirm the towel bars should be installed following the mounting height per 4/A600. | Architecture | Final Reckoning | 2023-10-05
Electrical Vault & Bus Vault Elevation Section Cut (N/S) Ref: CIV0160 Provide section cut through electrical vaults & bus vault in north/south direction (sketch location #5) to clarify how vaults are to be installed in relation to the site grade elevation changes. Clarify if the vault tops are to be installed level, stepped up in elevation from electrical vault to elec vault to bus vault, or installed on an angle to match adjoining final grade elevations. | Civil | Fallout | 2023-10-07
Paint Substitution Request See attached substitution request from Sherman Williams to provide the deep base colors P3-P5. | Architecture | Dead Reckoning | 2023-10-10
Nursery Headwalls Are the nursery bathrooms supposed to be handicap accessible? If so how would the design/dimensions of the headwalls change? | Architecture | Ghost Protocol | 2023-10-05
Lab Gas Manifolds - Special Gas The lab gas drawings show piping labeled as "SG" for "special gas." Please advise which special gas will be used in the building, serving the manifolds at the (2) locations on the 5th floor and (2) locations on the 6th floor, as each gas requires a specific manifold. | Plumbing | Final Reckoning | 2023-10-04
TO Ledge Clarification at Western Point Reference A102_S and attached RFI from the concrete subcontractor, Miller & Long. The 3D model shown in the snip below has the ledge at 60.75â€™ and the updated slab edge has it at 60.5â€™. Please confirm which is correct. | Structural | Dead Reckoning | 2023-10-08
Existing Patio Plank Elevations Please see attached and advise on which noted slope is acceptable. | Civil | Rogue Nation | 2023-10-05
BCI RFI 2 Sheet H201 coded not 5 calls out the relief damper. Specification 23 09 93 Sequence of Operation, section 3.02, E Occupied Operation, paragraph 6 Relief Damper Control call for damper to be modulated based on building pressure. However, after a site visit itâ€™s been determined that the damper noted on H201 is a barometric damper that dumps into the mechanical room. Please advise. | Mechanical | I | 2023-10-04
Level 2 CMU Wall Height at North Existing Building SK&A response comment on Congressional Brick Angle Shop Drawings submittal 05 5000-032-1 conflicts with the contract document detail (3/A-508) for the Level 2 CMU wall at existing north building. The SK&A comment calls for the CMU wall to be full height while the contract detail shows the top of the CMU wall at 6'-0" and S6/EM2 framed wall above (to the underside of the Level 3 slab. Please confirm the SK&A comment shall be followed and the CMU portion of the wall shall be extended to be full height (to the underside of the Level 3 slab). | Structural | I | 2023-10-10
PHASE 1 OPENINGS MISSING FROM SCHEDULE Openings 41122-1, 41123-1, and 41035-1 appear on sheets A409-1 and A411-1, but are not shown on the door schedule A602. Please confirm door and frame material, door elevation, hardware set & jamb/head/sill details. | Architecture | Dead Reckoning | 2023-10-02
Upper Brow Steel Queries Are any additional support posts necessary in the inside corner referenced in the attached document? Is the dimensioned angle extension sufficient for the deck support? Please advise. | Structural | Dead Reckoning | 2023-10-05
Color Change for Enterprise Bench Data Jacks Confirming RFI: Per Kewaunee, they have discontinued the grey bezels and housing for the data jacks. The only colors available are black or ivory. Per phone conversation with Will on 7/27/2023, it is acceptable to switch to black. | Communications | Rogue Nation | 2023-10-05
8" Storm Line Corresponding Structure There is an 8" storm line that runs from the roof down through the underground dock, see sheet P11-00A. There is no continuation of the storm line in PR-49 & PR-49A on sheets C03-00 & C04-00. PR-49 does not have connecting pipe that corresponds to P11-01A.1. Currently there is no corresponding structure to get water out of the footprint. Please advise. | Civil | Ghost Protocol | 2023-10-04
Steam Trap & Steam/HHW Details We cannot find a detail for desired typical steam trap assemblies nor a detail for the Steam/HHW Heat Exchangers. | Mechanical | Ghost Protocol | 2023-10-09
BP02 - Concealed overhead stop door hardware There's one thing that came up that will need a response from the architect. They specified a concealed overhead stop in hardware set 56 for doors 2108, 2109, 2110, 2111, 2112, 2113, 2114 and 2115. However your existing frames to be re-used do not have any concealed stop preps in the headers. | Architecture | Ghost Protocol | 2023-10-04
Amenities Toilet Partition Clarifications 1. The West building PH Women's Restroom door was approved at 24" width. It was reduced to 22" to accommodate field dimensions. Please see drawings in RFI reference and confirm acceptability. 2. The East building ASI toilet partitions are to be Black 2000C, and the West building ASI toilet partitions are to be Burnt Strand 5107. Stainless Steel hardware can't be painted black. Please see color sheet in RFI reference and confirm partition panel colors and stainless steel hardware are acceptable. | Architecture | III | 2023-10-04
Domestic Water Valve Location in the new tunnel See attached. should this valve be relocated closer to the main to eliminate the dead leg at the future tie in? | Plumbing | Fallout | 2023-10-09
Level 2M and Level 3 Mechanical Yard Louvers Clarification Reference sheets A5.08, A9.18, 2/A6.07, 3/A6.09, and returned RFI #173: Please verify what the sill condition is that these elevations will be installed and fastened to, and what the distance from the Face of System to Column Line J.6. See attached comments on Details referenced on returned RFI #173. | Architecture | III | 2023-10-01
EF-1.4 location Does the E02 window plan on getting demoed or should the new EF-1.4 be adjacent to the interior side of the window? | Architecture | III | 2023-10-10
Shaft Assembly Required for Stair 4 The north wall of Advanced Manufacturing 1312 and south wall of Stair 04 1319 are to be rated 1 hour and 2 hours, respectively. One of these walls must be a shaft assembly to allow both walls to be constructed, finished, and fire stopped. A/E to provide a new partition type to allow proper installation. | Architecture | II | 2023-10-07
Remaining Lvl 3 Phase C/D T-Stat Location Is the T-stat relocation in the phase D space (3009-3010) acceptable? This is done to place it under returns. Could desired T-stat locations be provided for the remainder of the phase C space? | Mechanical | III | 2023-10-06
Wall Condition for DWC-1 As currently designed the new F021 (1-1/2â€) wall at elevator shaft would be in alignment with ETR wall in Lounge 107 but we discovered a conflict with the ETR 3â€ elevator call button panel that will not fit in the new F021 wall. To resolve elevator call button conflict and keep both walls in alignment; Donohoe is proposing changing elevator wall and ETR south wall of lounge 107 to F033 wall type. Please note increasing wall depth at Lounge 107 will affect wall alignment with the window frame on the west wall. Please confirm proposed suggestion is approved. | Architecture | Ghost Protocol | 2023-10-04
Ground Floor Layout Issue Ground floor E layout â€“ Walls do not align with column at recessed entry as shown on drawing. | Architecture | Ghost Protocol | 2023-10-07
ARCH - L100 Kitchen - Location of ELEC panel Currently there is an electrical panel located on a wall that is too close to proposed casework and a door frame. Can this panel location be moved to create enough space as required? GBBN to review location in meeting on Thursday 09/15/2022. | Electrical | Dead Reckoning | 2023-10-08
AHU-1/HP-1 Max Run Length The specified and submitted AHU-1/HP-1 has a max refrigerant pipe run length of 66', which cannot be achieved with the current layout. The distance from the roof to the 3rd floor through the shaft will be approx. 30', and then it is approx. 60' from the shaft to the AHU location. Please provide a revised spec. | Mechanical | I | 2023-10-04
3 Way Dimming Requirement for Light Fixtures per Bulletin With the current switching devices the dimming can only be accomplished from one location, see approved cut sheet. The rest of the switches have to be regular switches, non dimming. Please confirm this is acceptable. 3 way switching was not added until bulletin set drawings and if 3 way dimming is required weâ€™ll have to change to a low voltage device. Also confirm if a ceiling censor is required on the high ceiling. | Electrical | Dead Reckoning | 2023-10-02
Level 2 and 3 Coiling Door Support Clarifications Reference EOS1.04 and submittal 055000-031-0: 1.) Misc metals submittal referenced above show 13 pier under the 4"X6" vertical tube steel at elevation 419'5". None of these piers are shown on the architectural or structural drawings. Please advise. 2.) On EOS1.04 there is a continuous 8" curb shown and on the attached copy, M&L is showing the added grades per blow-up details on 2, 3, and 4 on the left side of the same page. These details provide the grades of the curbs. Detail 4 has a step from 419'5" up to 419'8". Please confirm the location of the step, and confirm top of curb elevation along 9.2 line east of the opening in the curbs. 3.) On the misc metals submittal referenced above, there is an elevation given (439'9"). The top of the slab is at 441' with a 9" slab and 6" drop panels. The elevation shown is for the drop panel, however, there are only drops near the columns. Please confirm the 439'9" elevation for the top of the vertical tube steel only applies where drop panels occur, otherwise the top of the vertical tube steel should hit bottom of slab at elevation 440'3". | Structural | II | 2023-10-05
SPD Cooling Zone North Wall Fire Rating Floor/Wall Joint The drawings call out for the existing smoke tight wall in SPD cooling zone to be brought up to meet a 1 hour fire and smoke rating. The detail shown in the drawings specify that the bottom of the wall to floor joint be filled with sealant. This has been achieved in the construction side, but in order to properly achieve this on the backside, we must take over the Pharmacy Breakroom, and perform demo of the existing base, flooring, and 2 wing walls. Looking further into the UL 400 series walls fro the Purple Book, the wall systems identify this bottom of the wall joint as "optional". Please see attached. Is it acceptable to make this joint sealant at the bottom of the wall optional to avoid the demo of the Pharmacy Breakroom finishes which will lesson our impact in their space? Note: This work would be scheduled the week of the 19th to do fire stopping on the back of the wall so we would like an answer prior to the 13th of July to schedule the additional work if needed. | Fire Protection | Ghost Protocol | 2023-10-03
BP8 Generator Lighting Please see the attached drawing with proposed locations for light fixtures in the north garage lawn generator area. These light fixtures would be fed out of the generator panels and would be Lithonia LIT BGR-LED-P2-40K-MVOLT-PER-DNA-M2. Please advise if this is acceptable. | Electrical | Fallout | 2023-10-04
Header at Corban Elevation Is there a steel header missing at the top of the proposed jewel box opening along the Corban elevation of the building? Currently, there is no new steel shown to support the existing beam along column line B.E. | Structural | III | 2023-10-04
JLL VAV Confirmation HVAC Subcontractor has requested for JLL to confirm the (4) VAV's onsite in their possession are brand new and have never been used to ensure they will work. Also, Please confirm with the Mechanical engineer where these (4) VAVs will be installed and what (4) VAVs they will replace per the drawings. | Mechanical | I | 2023-10-01
Fire Protection - 12.6.23 1) Can we use the â€œsmall room methodâ€ (NFPA 13, 2013 Sec: 8.6.3.2.4-8.6.3.2.4.1)? 2) Can we use the â€œdesign area reduction for quick response sprinklersâ€ (NFPA 13, 2013 Sec: 11.2.3.2.3.1)? | Fire Protection | Rogue Nation | 2023-10-07
S1.141 and S1.142 Steel Beam Reaction Clarification Would like to clarify that the reactions shown in the sheet notes (highlighted in yellow) apply to the beams highlighted in yellow in the attached document. Those reactions were used at the IPF roof and I would to clarify that they apply to the APC roof as well. | Structural | Rogue Nation | 2023-10-08
VENTILATION FOR REMOTE REFRIDGERATION RACK in response to ASI #141 . Please refer to the approved remote refrigeration rack submittal. The approved submittal calls for 1140 CFM of ventilation required for the room at 90F ambient temperature. The mechanical drawings do not show any cooling or ventilation for the room the remote refrigeration rack will be installed in. per PC Godfrey, The HVAC system is providing a 1â€ CW supply and return line with a shutoff ball valve termination in the room. The building HVAC chilled water supply will be supplying the design chiller discharge water temperature @ 44 degrees for building CW system loop from the central plant. The HVAC system has not incorporated any means to warm / cool water temps, and or adjust the water pressures and flow rates at the 1â€ shut off valves. Please advise. | Mechanical | Fallout | 2023-10-08
Bathroom Damaged framing We believe framing rusted out in bathroom locations will need to be replaced. Please advise | Structural | I | 2023-10-10
F2 Bench Mounting Preference No mounting preference was selected for F2 Bench in response to submittal 320000-002-0. See attached sheet from submittal with mounting options and confirm selection. | Interior Design | Ghost Protocol | 2023-10-01
Women's Locker Room Mirror Design Please advise the desired mirror design for the women's locker room. | Interior Design | Final Reckoning | 2023-10-08
West Stairs Ground Floor Space Behind Room 40034 Per our Building Inspector to have access to under stairwell behind Room 40034, there needs to be a minimum of 24" clearance between the sheetrock and the stairs. | Architecture | Dead Reckoning | 2023-10-01
Level 3 Box-out Issue for TE-02 and OA-02 Reference sheet A1.05, M1.05, and returned submittal 013100-004-0: Given the mechanical subcontractor did not shift the box-outs per architect comment on returned Level 3 sleeve drawings, the TE-02 and OA-02 riser opening on Level 3 need to be shifted. The shift is due to the current duct locations conflicting with the toilet carrier in the ADA restroom. This will require concrete removal and cutting of rebar in order to create the necessary openings. See attached Images for more information on the opening sizes. Please confirm cutting the slab at these 2 opening is acceptable (scan layout included). | Structural | Rogue Nation | 2023-10-09
Location of detail 4 on A-621 The reflected ceiling plan for rooms 3101, 4101, & 5101 (8 on A-443) reference a section detail 4 on A-621, however there is no 4 on A-621. It seems that it is intended to reference detail â€œHEAD HO5â€ detail on A-621, please advise. | Architecture | Final Reckoning | 2023-10-06
DOAS Supply and Exhaust Duct Insulation We need to confirm if the duct work coming from the DOAS unit running down the building needs to be insulated. It is Driekast's interpretation that since this duct is inside the building envelope insulation is not needed. | Mechanical | Rogue Nation | 2023-10-04
Rain Screen System Close off Current jamb detail of stair 2 curtain wall and south facing alcove elevations shows the rain screen system to be going inside the building / behind the wet line of the curtain wall system. Messer suggest turning a jamb stud and adding break metal to close off rainscreen system. This may affect the RO width of the curtain wall. Please advise. | Architecture | Rogue Nation | 2023-10-01
Bldg 2 Temporary Leasing Space Pre-Bid RFIs Reference is made to drawing set: Aspen Heights College Park - Temp Leasing Permit Set_04.21.2023. Please advise on the attached list of RFIs stemming from the temporary leasing space drawings. There are also field photos in that attachment for reference. | Architecture | I | 2023-10-07
Bldg 2 Temporary Leasing Space Pre-Bid RFIs Reference is made to drawing set: Aspen Heights College Park - Temp Leasing Permit Set_04.21.2023. Please advise on the attached list of RFIs stemming from the temporary leasing space drawings. There are also field photos in that attachment for reference. | Architecture | III | 2023-10-05
Bldg 1 Lobby and Collab Room Exposed Ductwork Reference is made to B1 1/M3.00 and RFI #272. Similarly to the R101 Lobby at Building 2, an exposed duct is specâ€™d to be installed at the ceiling of P104 Residential Lobby at Building 1. Please advise whether this exposed spiral duct is to be interior insulated duct as well. | Mechanical | Rogue Nation | 2023-10-03
G1 Phase 2 Lighting Fixture Type FF02 Location Clarification Interior design drawing IN204 and electrical drawing E224_D indicate location of lighting fixture type FF02. This placement cuts through a wall so the fixture is half in one room and half in a closet. Please advise on location of lighting fixture type FF02 in level G1 and provide dimensions and mounting details. | Electrical | II | 2023-10-06
HD Pavement Take a look at the marked up PDF, Prus is looking for clarification in the HD Pavement section. It appears there is Pedestrian paving as well as an unknown hatching. Can you have the design team confirm that this is their intent. | Civil | III | 2023-10-09
Potomac Room Doors & HW Please provide specs for the (2) new sets of Potomac Room doors and new hardware for these doors. Please note DCC has (6) hinges, (1) closer, and (1) exit device that was going to be used for the reversed existing door (see attached for specs). We assume you'll want to reuse this for the new doors. | Architecture | II | 2023-10-02
Level 2 SE Terrace out Door Receptacles Clarification Reference sheets E1.04A, A5.03, and 3/A6.22: Architectural drawings show a glass railing system along the balcony of the second-floor outdoor area. Sheet E1.04 shows multiple receptacles located along this railing system. Per detail 3/A6.22, there will not be enough room to install receptacles (4" min required). | Electrical | Fallout | 2023-10-03
Unit 1408 Pipe Outside of Soffit In unit 1408 there is a pipe that reduces from 6" to 4" in the ceiling above the kitchen and transits across the entry door/ foyer area where it is supposed to be concealed inside a soffit area. The pipe is installed per coordinated drawings at 9'-1/4" off the control line, however this places the pipe outside of the soffit and in the exposed ceiling area in 1408. DCC recommends rerouting this pipe to run south of the 4" storm line so it will no longer be exposed. | Plumbing | II | 2023-10-02
Door Openings Per door schedule on sheet A 611, 110 A & B are shown as 3-0 x 8. Opening is only 7â€™-0â€ high. Does this opening need to be modified, to accommodate taller door, or ill a 3-0x 7 work? | Architecture | II | 2023-10-07
Construction Joint in Mat Foundation Please confirm it is acceptable to break the mat foundation into two pours per the attached marked-up drawing. | Structural | Ghost Protocol | 2023-10-06
Construction Joint in Mat Foundation Please confirm it is acceptable to break the mat foundation into two pours per the attached marked-up drawing. | Structural | II | 2023-10-05
South Stair Hanger in Shaft Assembly This RFI is about the south stair hanger rods that are in the shaft liner. Per conversations on the last site visit, a drawing is attached of the proposed solution. This is seen on the north stair shafts of floors 2 and 3. | Structural | Final Reckoning | 2023-10-01
CUB Hot Dipped Columns In the Specifications 22FHLE01-ST-SPC-003 - Structural Steel Framing, under 2.9.A section. It mentions the Hot-Dip Galvanized finish for all exposed structural steel. In the drawings (attached) it shows four columns at the cooling towers structure that are main building columns which will need to be hot dipped for the full length. Are there any concerns on these four columns being hot dipped versus being primed painted in regards to appearance in the building? | Structural | Ghost Protocol | 2023-10-01
GFRC Substrate Confirmation Ref: A322 Per Justin Drywall's Structural Engineer, plywood sheathing is required as the substrate for GFRC locations to allow proper framing attachment. Drawing A322 is currently depicting an exterior grade sheathing at all GFRC locations. Please confirm if it is acceptable to install plywood sheathing ilo ext. grade sheathing at all GFRC locations. | Architecture | I | 2023-10-06
BP04 - Physician Lounge Existing Flooring See attached. The indicated rooms show the flooring to remain. This carpet appears stained and of poor quality. Is it the intent to keep this flooring or replace it? | Architecture | III | 2023-10-06
MOUND - SHEAR DESIGN LOAD CRITERIA Structural Steel Note 2 indicates that "Unless specific end moment and reactions are indicated on drawings, design and fabricate connections to resist based on the maximum uniform load capacity of the member for the span increased by 15% but no more than the shear capacity of the member". However, Plan Notes on Framing plans indicate to design connection for 10kips if reactions are not noted on the plan. As such, on where no actual loads are provided, connection design shall proceed as follows: a. For beams W8 to W14, connections shall be designed for minimum of 10kips. b. For beams W16 and above, i. Connections shall be designed per 65%UDL for vertical shear reaction. ii. For short beams where equivalent 65%UDL are high, capacities shall instead be indicated on full report for EOR's verification. c. For channel beams C8 and above, connections shall be designed for minimum of 10 kips. d. For beams C5 and C6 where 10-kip minimum shear load might result to heavy connection, capacities shall instead be indicated on full report for EOR's verification. Please confirm that above proceedings are in line with EOR's intent. Otherwise, please provide actual vertical reactions(LRFD) at each joint See attachments | Structural | II | 2023-10-08
Level 16 Brick Angle Clarification Reference sheet S1.12, details 7&11/S7.07 and returned submittals 055000-036-0 and 055000-038-1: On S1.12, detail 7/S7.07 shows brick angle attached to C6X8.2 hanger part of kicker assembly intended for above Level 15 window openings. Detail 11/S7.07 shows brick angle attached to Level 16 slab edge which is intended for brick piers. Per conversation between DCC and design team, the different elevations shown in these 2 brick angle details may cause water tightness issues and aesthetic concerns. Please confirm brick angle should be installed at a single elevation continuously. If confirmed, please update details accordingly. | Structural | Rogue Nation | 2023-10-09
RFI 022 - Domestic Water Balance Valve On sheet P5.01-P1 Plumbing Equipment Schedule (Balancing Valves â€“ 221119) (BV) lists a Circuit Solver Model SC-U-A-S-3/4â€â€“ 110 CV1 to be installed where indicated. However, this valve is not listed in the specifications. Please advise. | Plumbing | Fallout | 2023-10-10
Existing Chimney Support Beam in South Locker Room A. The W8X18 beam in RFI-023 response can only be installed two ways because of the shoring needed to support the existing load. Option 1 was to shore the beam from above, but this couldnâ€™t be done because the club will not allow the area needed above to be closed off. Option 2 would be to needle shore from below(See attached Shoring sketch in files) To achieve this shoring the W8x18 beam will need to be redesigned to coordinate with needle shoring. Suggestion: Lower W8x18 beam to accommodate for the needle shoring, allowing second point of contact. Then add additional post to catch W8X18 beam in dead space area.(Page 1) B. We would also like to install two selves through W8x18 beam for two 4â€ conduits. Please advise if this is approved and of any requirements that need to be meet for the sleeves. C. What is the design load for the vertical wall above. (Page 3) | Structural | Ghost Protocol | 2023-10-07
Concrete Repair Existing Garage Please provide job specific detail for each of the following conditions for repair of existing garage degradation: -Grout pocket -Vertical and overhead concrete repair -Horizontal repair -Epoxy injection | Structural | I | 2023-10-01
Gilbert Knox Box Location Provide location of where the Gilbert building Knox box is to be set. Also, there currently is a Knox box on the entrance gate. Can this be used? | Fire Protection | Ghost Protocol | 2023-10-01
Drain Line Tie-In Point Please advise if the drain lines for the sink and environmental chambers located in the Connected Care Lab can be tied in to an existing nearby 4" FRP Aqueous Waste line instead of where shown on the 1st floor plumbing plan (see attachment). This would eliminate core drilling one of the drain lines in an active telecomm room below while also preventing us from having to run pipe above existing ceilings on the first floor. Additionally, please confirm the drain line for the environmental chambers can be FRP like the sink. | Plumbing | I | 2023-10-04
Color of Ceiling Devices in Pub There are several white new and existing ceiling devices to go in the Pub, which has black ceiling tile. What color should the following ceiling devices be? - New supply and return grilles - M301 shows color to be white - Existing speaker covers (in project scope to remove and reinstall only) | Architecture | I | 2023-10-02
Level 1 Post Install Plates for Grand Stair Reference returned submittal 057000-001-3: Per SER comment on returned submittal, please confirm the post install locations shown in snippet and GPR scan photos below are acceptable. Note the scans were performed on the structural slab (topping slab was boxed out at these locations). | Structural | I | 2023-10-01
PRV- CHW System Please see attachment for further explanation. The concern is that if the chilled water system was down for whatever reason, the CHW system water would raise in temperature causing the system pressure to rise that could potentially result in failure. Should a PRV be installed in the system? | Mechanical | Fallout | 2023-10-08
South Entrance Canopy Drain Issue Similar to RFI-306, the south side canopy drain is too low and will interfere with the metal panel soffit. Please advise how to proceed. | Architecture | Ghost Protocol | 2023-10-08
Above Cabinet Lighting LED Tape Lights Cabinet lighting sub suggests using linear LED tape lighting in a shallow mounting channel for the above cabinet lighting. This will be easier to install, is field-cuttable to whatever length is needed and will be less expensive than the Maxlite undercabinet lighting that we are using. Also, as this is indirect ambiance lighting, not the main light source, they recommend the 1.5W/FT as opposed to the 4W/FT Maxlite. Please review the two options provided for LED tape lights for above the cabinet lighting. Option #1: Nora Lighting LED tape light in a mounting channel, 1.5 watts per foot 3000K LED with a hardwire LED driver to be mounted in one of the cabinets. This tape light comes in a 16â€™ roll and is field-cuttable to whatever length is needed. The mounting channels are also field cuttable. Option #2: this option is the same as option #1 however, instead of a hard-wired driver, this option comes with an all-in-one LED driver/ dimmer switch so that you would not need to place the driver inside of a cabinet. | Electrical | I | 2023-10-01
ED Drilled Pier L-13.4 Within the returned drilled pier submittal from Sherzinger it appears that drilled pier L-13.4 (or drilled pier 56 on their shop drawings) was deleted. CPR-014 does not show this deletion. Is this deletion correct? | Structural | III | 2023-10-01
Stainless Dishwasher Duct Wrap Due to conflicts with existing elevator conduits and 4â€ thickness of fire wrap, can stainless dishwasher exhaust be wrapped and sealed with standard duct wrap, instead of 4â€ fire wrap. See photo indicating duct. Advise if standard duct wrap can be used. | Mechanical | Ghost Protocol | 2023-10-10
Pull box in stair well AV drawing AV109 indicates 36" x 36" pull box to be placed above hard ceiling in stairwell. This will require conduits to be routed through the stairwell and a panel to access pull box from stair landing. Can you please confirm this placement? | Communications | III | 2023-10-09
North and South Exterior Wall Blind Side Cavity Drainage and Terminations DCC received CCD #15 on Thursday February 2, 2023 which provided some additional detail for drainage inside the cavity between the existing building facades and the new construction exterior walls. Please advise on the follow up questions related to the backfill in the updated details. - Question #1: What material is the backfill? Concrete? Drainage Piping? Etc. - Question #2: Confirm the backfill shall be sloped at 1/8" per foot, similar to the backfill at the north foundation wall. In addition to the questions on "backfill", additional information is required related to the extent of the "backfill" and terminations at the low points of the backfill. There are three separate conditions for the blind cavity between buildings. On the south side there are two conditions; one between existing building wall and new construction exterior wall (Condition #1), and one between existing building wall and bio-retention planter wall (Condition #2). On the north side the condition is existing building wall and new construction exterior wall (Condition #3). - Question #3: Please advise where the low and high points of the "backfill" shall be. - Question #4: Please provide details depicting terminations of the backfill drainage. | Civil | III | 2023-10-07
Access to Soft Water Line The building owner has requested a point of access to the soft water piping which runs vertically, located in the suite intake area south of the mechanical room. The contract drawings currently call for pipe to be enclosed in a on all sides. | Plumbing | Ghost Protocol | 2023-10-06
Parking Garage - Pour Break (Section 3/402 & 4/S402) This RFI Is Due By 6/28/2023. For section 4/S402 and 3/S402, I would like to confirm that it is acceptable to have a pour break between the beam and the wall as I show with the red line in the attachment. If this is approved, I can add water stop at this joint since it is below grade. Please advise. | Structural | Final Reckoning | 2023-10-06
DETAIL 9/S514 - ANCHORS HITTING ELEVATOR SHAFT REBAR Please see attached. When drilling the holes for the epoxy anchors, many of the holes are hitting the vertical & horizontal rebar for the elevator shaft. can new holes be drilled in to the channel to miss the rebar? if so, what is the minimum & max distance the new hole spacing. | Structural | II | 2023-10-09
STAY-FORM USE AT BULKHEADS Is it acceptable to utilize a stay-form ILO plywood and shear key as detailed on the documents? | Structural | Fallout | 2023-10-02
Common Area Thermostat Location Confirmation Please confirm that the common area thermostats should be located 54" above finish floor at locations indicated on the floor plans. | Mechanical | I | 2023-10-10
Common Area Thermostat Location Confirmation Please confirm that the common area thermostats should be located 54" above finish floor at locations indicated on the floor plans. | Mechanical | Rogue Nation | 2023-10-10
ED Courtyard Slab Elevation Please note -- this is hot and affects excavation being done on 10/12. At the ED building foundation, there is no note provided in the Architectural or Structural drawings to indicate the elevation of the Courtyard slab. Please clarify this elevation. | Civil | Ghost Protocol | 2023-10-06
Innovox Audio MLA-8 Please clarify where the (2) Innovox Audio MLA-8s go and what they will be mounting to. | Communications | II | 2023-10-01
Bond Beam Location at Typical CMU Wall Per 'Typical CMU to Bottom of Deck (Beam Parallel + Perpendicular)', on Sheet S-502, the bond beam is captured to be installed directly below framing. We would like to bring bond beam down one course. Please reference attached and confirm if acceptable. This RFI needs to go directly to DOR, Mason & Hanger. | Structural | II | 2023-10-08
Corner Guards There are two different notes in the drawings that reference corner guards. The first note from sheet G-002 calls out corner guards on all outer corners of walls in labs and LER. The other note from A-600 states that they should be at all outside GWB corners. Please confirm which note should be followed. | Architecture | Ghost Protocol | 2023-10-03
SPD Cooling Zone Sterilizers B605B-MP Light FOR RECORD: Per our walk last week with SES/ Design Team, we are going to change light W1 in B605B-MP from a 3 foot model to the 2 foot model due to the insulation thickness on pipes not allowing the 3 foot light to fit. Updated product data to come. | Electrical | I | 2023-10-06
Bldg 2 Semi-Recessed Trash Can Conflict in Women's Restroom Reference is made to Bldg 2 A0.04 and A1.12. During our walk in the lobby Womenâ€™s Restroom with the Katie (BSB) it was discovered there is no location within this restroom where the semi-recessed trash can and paper towel holder can be installed due to ADA code compliances issues. Katie proposed omitting the semi-recessed trash can all together and installing a stand-alone trash can and paper towel box that can sit on the sink. Please confirm this is accurate and provide the specs for the trash can and paper towel box. | Architecture | Dead Reckoning | 2023-10-10
Existing Domestic Backflow Preventers As a part of Bid Package 6A, new backflow prevention has been added downstream of the new meter pit installed South of Goodman Avenue. The new 8" backflow preventer is upstream of the (2) existing 6" backflow preventers in the CCP Emergency Turnaround. Confirm that the existing backflow preventers are no longer required with the installation of the new device upstream. If no longer required, a cost will be provided to UCH for a decision if they should be removed as a part of this project. | Plumbing | Ghost Protocol | 2023-10-10
Level 3 Rebar Reinforcing Discrepancies - M&L RFI #169 There are many discrepancies between Miller & Long's rebar shop drawings for level 3 and the contract drawings. Please confirm the mark-ups to the level 3 shop drawings are correct and issue an updated structural drawing to reflect these changes. | Structural | Rogue Nation | 2023-10-02
Pre-Set Lighting Scene Requirements During the OAC on 1/24/2023 there was a discussion about pre-set lighting control scenes and if they are required on this project. Please confirm that per specifications this is not required. | Electrical | Fallout | 2023-10-02
Lintel requirements for delivery item What are the lengths for all of the lintels we are providing? | Structural | Ghost Protocol | 2023-10-08
Lintel requirements for delivery item What are the lengths for all of the lintels we are providing? | Structural | Fallout | 2023-10-07
Structural Review What Structural response is needed | Structural | Ghost Protocol | 2023-10-07
Closer Interfering with Glass on Door 005-1 Door 005-1 on the ground floor is the have an HG elevation. This door is have a coordinator and a surface closer. In order for the closer to get around the coordinator the closer needs to be mounted to a drop plate. This closer will cover the glass by 1". Is this acceptable as ordering a new door will have long lead times. | Architecture | II | 2023-10-03
Stair 1 Standpipe Clarification See requested attached diagram of Standpipe/Sprinkler Piping Relocation from Wolf Fire Protection per comments on response to RFI-352. Please confirm if the proposed piping rerouting is acceptable. | Fire Protection | II | 2023-10-02
CFMF Sealer Gasket Location Confirmation Ref: Spec 054000-subsection 2.9E, attached RFI Spec section 054000, 2.9E, states that Sill sealer gaskets must be "Closed-cell neoprene foam, 1/4 inch thick, selected from manufacturer's standard widths to match width of bottom track or rim track members as required." It is not clear on the partition schedules or exterior details where this material is scheduled to be installed. Please advise where the referenced sill sealer gaskets referenced above are to be installed. | Architecture | III | 2023-10-10
Curtain wall and sunshade Please see attached photos. Architectural Glass and Metal the subcontractor for the curtain wall has let us know of possible savings by switching to alternative finishes on the curtain wall framework and sunshade. This subcontractor performed the work on the new endoscopy building and informed us if we wanted to match the finish to the endoscopy building then we would need to switch products. Currently, the finish is a custom sunstorm mica color on the curtain wall and sunshade. AGM has proposed to switch to a class 1 clear anodized finish in lieu of the custom sunstorm mica color on the curtain wall framework. With a savings of $58,356.00 and Valspar 339A854 bright silver paint to match the clear anodized on the sunshade. With a savings of $33,090.00. | Architecture | Ghost Protocol | 2023-10-04
ISOBIP Circuiting The isolation panel ISOBIP has two separate sides, fed from two separate sources. Each side of the panel can accommodate 16 circuits. How should we circuit the field devices? Do we divide them up evenly - circuits 1-16 on one side and 17-36 on the other? | Electrical | Dead Reckoning | 2023-10-04
Typical Dwelling Unit Mechanical Closet M-500 The Typical WSHP detail shows the units being mounted to the wall with Kendorf /uni-strut supports above the water heater. Please advise how these units should be mounted. | Mechanical | Ghost Protocol | 2023-10-05
Conduit Upsize for (8) Data Cable Locations Per previous discussion with the design team, please update drawings, upsizing rough-in conduit from 1" to 1-1/4" for locations with (8) data cables. These are indicated as "Type F" on the Telecom Drawings and Cabling Legend (T-002). | Communications | III | 2023-10-07
Stairwell Light Fixtures Mounting Height Please advise on the mounting heights of the light fixtures located in the stairwells. | Electrical | III | 2023-10-06
Nurse Perch Supply Interface Removal Per phone conversation yesterday we propose removing the supply interfaces from the lower section of the nurse perches on all floors. See attached drawing for mark ups on suggested locations of data and power outlets. Please confirm these changes are acceptable. | Electrical | Ghost Protocol | 2023-10-04
SE Radius Soffit Panels Please provide a reflectied celing plan/joint layout desired for the SE Radius soffit metal panels | Architecture | Ghost Protocol | 2023-10-10
Plan South Exterior Wall Louvers Please advise if lintels are required for the (2) mechanical louvers being installed in the Plan South exterior wall. | Structural | Ghost Protocol | 2023-10-03
MC 18-45.8 Channel Breaks In the returned Interior Structural Steel Framing submittal, JPS states to break the MC18x45.8 at column F-7 to let the beam (7B1) to rest on embed. similar to F-F. Please advise if it is acceptable do the same detail (without the beam) at C-7 & F 7 on both sides of column with the other channels MC 18x45.8? See attached | Structural | Fallout | 2023-10-07
FOR RECORD: OR ISO Panel Alarms FOR RECORD: The OR Staff notified Messer, POM and AH Leaders of alarms coming from the ISO Panels in ORs 14-17. After investigation, Adams Electric concluded this alarm was a nuisance alarm coming from the dimmer switch that is tied into the BASX Lights. In order to resolve the alarm being activated, the design team has presented three options: Option 1: Provide a new 277V circuit with an enclosed circuit breaker with ground fault outside of panel. Option 2: Provide a new 277V circuit with GFCI device in line with basex lights Option 3: Provide thermal rated ahead of current dimmer switch. Per discussions (See attached Email), it has been determined that the option most desired is option #3. | Electrical | Final Reckoning | 2023-10-07
B2 & Laundry CU Mounting Please confirm the CU's that serve Unit B2 and Laundry Room may be mounted with brackets that attach to the side of the building in the alley in lieu of mounting on the ground. | Mechanical | Dead Reckoning | 2023-10-08
USPS Key Keeper A USPS representative visited the jobsite on 12/6/23 and identified that a Key Keeper would be required at the exterior of the building mounted between 42â€ and 52â€ AFF to ensure USPS access to the building in case no concierge is available to provide access at the time of their delivery. No Key Keeper is currently within the scope of the project. Please confirm the USPS regulations requiring a Key Keeper for this project and issue an ASI to confirm that a key keeper should be added to the scope of the project including a specification for the product and confirm the mounting location at the N St side of the building adjacent to door 101. | Architecture | I | 2023-10-07
Patio Expansion Joint Caulk Spec Please provide a spec for the expansion joint caulk need at the patio extension. | Architecture | Ghost Protocol | 2023-10-01
Bldg 2 Elevator Smoke Curtain Soffits Reference is made to RFI 158 and the attached field photos. Please confirm soffits are no longer required around the Bldg 2 elevator smoke curtains given the smoke curtain's factory finished cover. | Architecture | Dead Reckoning | 2023-10-10
G1 Overhead Coordination Clarifications Reference P1.02 and attached: Please confirm bottom of pipe (BOP) elevations and provide solutions to the (14) issues shown in RFI. | Plumbing | I | 2023-10-05
Outlets/J-Box Locations at Bar Area The electrical at the bar area shown on the Food Service Drawings does not match what is shown on the Electrical Drawings. Please provide locations/elevations for all outlets and J-boxes at the bar. | Electrical | Rogue Nation | 2023-10-08
G1 Clubroom and Sky Lounge Draperies Conflict 1. The Clubroom in the G1 West North Lobby has an exposed pipe below the ceiling at 11" height in the pocket. It is in conflict with where draperies along the north wall should be installed. Ceiling height for the pocket is at 11'-8" as specified in interior RCP plans. Please see RFI reference for location and image of pipe and please confirm acceptability of splitting the draperies and running them against either side of the pipe. 2. In the Sky Lounge the draperies cannot be installed behind the columns. Please see the new layout attached (page 2) and confirm acceptability of running the draperies against the columns as shown on the layout. | Interior Design | III | 2023-10-09
Existing Traffic Signage There are four speed limit signs along the QTA and one merge sign along the GTC within the construction limits. Locations of these are indicated by the yellow circles in the attachment. Please confirm the traffic signs are to be demolished, NOT salvaged. | Civil | Fallout | 2023-10-02
Grouted thru-bolts During our review of the structural steel bids the contractor brought up the requirement to fully grout the thru-bolts on the tube steel slab extension. This can be seen on detail 2/S4.01 in the bid/permit drawings. The question was is this required and to please clarify the intent. This detail differs from Calhoun and was not shown on the 75% GMP Siddall drawings; so it was not covered in the GMP. This requirement will have a major cost and schedule impact. | Structural | Fallout | 2023-10-10
Duct Detectors Confirmation Per code the duct detectors are not required given the CFM of the 4 units in the Keller Williams space (Less than 2000CFM). Please confirm if this is a building requirement and how to proceed. | Mechanical | Ghost Protocol | 2023-10-07
Exterior Skin of ED The east elevation of SI calls out the removable panel with hatching and a note that describes the knockout panel. The North elevation of ED shows corresponding lines in the metal panels but no note or hatching is included. Are these to have knock out panels or for the third floor for ability to add ribbon windows in the third floor shell space? Please advise. | Architecture | Dead Reckoning | 2023-10-04
Level 13 Unit D1 Mechanical Layout Revision Reference returned RFI-043 and attached from returned submittal 238129-001-2: Please provide updated sheet(s) for the revised level 13 mechanical layout per RFI 043 response. | Mechanical | Ghost Protocol | 2023-10-08
Existing Foundation SA Work Ref: SSK-006, attached marked up A151.B 1. Existing Foundation Wall (along gridline 1 / D-E.5) Due to concerns regarding existing substrate material is inadequate for rebar dowel installation into existing wall per SSK-006 dated 10/30/2023. As a result of site conditions M&L has provide slight alterations for proposed repair detail for west foundation wall. Please review proposed detail and confirm direction (attached). 2. Existing Foundation Wall (along gridline 1 / A-D) Is structural alterations, ie shotcrete, required at west foundation wall along grid line 1 from A-D? See attached photo of site conditions. Please provide repair detail and extent of work. 3. Existing Foundation Wall (along gridline A / 1-2) Is structural alterations, ie shotcrete, required at north foundation wall along grid line A from 1-2? See attached photo of site conditions. Please provide repair detail and extent of work. | Structural | Rogue Nation | 2023-10-06
VAV box piping connection details Please provide the drawing and detail called out on K302 M1-1-333 for the VAV box connection details. Drawing K302-M4-1-604 was not included in the drawing set. | Mechanical | II | 2023-10-07
Cable Tray at 2nd Floor Non-Secure Area(s) We are requesting to change the cable tray layout at the 2nd Floor non-secure corridor(s). To meet all MEPS clearances, we are unable to stack the cable trays - as captured on Note 1 of T-123. Please confirm if the below versions are acceptable: - Opposite Sides of Corridor - Staggered Elevations (i.e. (1) at 9'-0" and (1) at 9'-6") - Opposite Sides of Corridor - Same Elevation The elevations mentioned above are targets and are subject to change. Please advise if above versions are acceptable. | Communications | I | 2023-10-01
Unit B8 & B8.1 Electrical Panel Location Conflict 8/8/23 - Feeders for the panels are unable to pass through ceiling space because of excess ductwork. The panel cannot be reached if it stays in the initial bedroom location. Please provide an alternative location or confirm the one provided is acceptable. ----------------------------------------------- An electrical panel is shown behind a bedroom door in unit type B8 and unit type B8.1 per E-354. Ductwork is above this same area per B8/B8.1 mechanical layouts, so the panel is unable to be installed behind the bedroom door. Please confirm the coordinated panel location within unit type B8 & B8.1 is acceptable (see mark-ups). Otherwise, please provide a new location for the electrical panels. | Electrical | Dead Reckoning | 2023-10-07
Shower Seat Grab Bars Please see attachment. The shower seat details do not call out grab bars, but the ADA details do show grab bars for the shower seat. Please confirm that we intend to install grab bars here and confirm the location. | Architecture | Dead Reckoning | 2023-10-07
Added Drain Between East and Center CY Walkway Per site walk on 5.30.23, weep drain is to be added in walkway between east and center courtyard. Drain is to be 4 inches with 2inch pipe and flush with WP and is to be concealed underneath pavers. Drain to tie into existing drainage below L1 | Civil | I | 2023-10-08
Flange color for Fixture Types L4 & L4B Please confirm that the flanges are to be white for fixture Types L4 & L4B. | Electrical | Rogue Nation | 2023-10-03
Existing Fin Tube Controls There are four existing fin tube loops with pneumatic controls within the Open Access lab area. FT3157 is within a room served by VAV-3155 while FT3150A, FT3150B, and FT3142 are within areas served by phoenix valves. How will these fin tubes need be controlled? | Mechanical | I | 2023-10-05
Requested Work Point Dimensions Please provide work point dimensions to locate sloped beams at canopy steel. | Structural | I | 2023-10-08
Chapel Building - Anchor Bolt Misplacement See attached. The anchor bolts for the HSS column were incorrectly placed. Kindly review and advise on remedy. | Structural | Ghost Protocol | 2023-10-04
Elevator 3 Pit Ladder Clearance See Attached for Documentation Purposes. | no | Dead Reckoning | 2023-10-07
Level 2 Stair #3 opening Level 2 stair #3 opening was unable to change in size as the pans were already set at this location. Sheet A8.C12 has this East to West dimension as 17'-2" S.O. instead of 16'-8". Could this be updated in an upcoming ASI? | Architecture | II | 2023-10-05
Unlabeled Material Under North and West Storefronts at Building 2 Reference is made to B2 sheets A2.01 and A2.04. Please advise what type/finish of material should be installed under the storefronts at the north and west elevation. Those small areas are not labeled. See attached marked up sheets for reference. | Architecture | Ghost Protocol | 2023-10-05
Bldg 1 Water Main Engineer Stamped Drawing Reference is made to attached image from our plumbing subcontractor. Please provide an engineer stamped drawing showing the water main coming though concrete wall with details of the anchors and thrust blocks. WSSC will not inspect until the engineer stamped drawing is provided. | Plumbing | I | 2023-10-06
Unit 1109-1409 Electrical Panel Location Confirmation There is an electrical panel in units 1109-1409 that is shown in MEP coordinated drawings to be next to the unit bathroom in a wall that is not wide enough to accommodate the panel depth. On sheet A405 E, the panel is shown in the wall next to the refrigerator. This wall is thick enough to accommodate the panel depth. Please confirm the panel location in the architectural drawings are to be followed. | Electrical | Dead Reckoning | 2023-10-06
Unit Exhaust Plenum Box Size Please provide the desired depth of the unit exhaust plenum box. Details 15 and 16 on M-501 (attached) do not indicate a depth for the box. | Mechanical | Dead Reckoning | 2023-10-09
Existing Steel Supports at Removed East RTU Supply Air Duct The old supply air ductwork for the old East RTU has been removed, leaving existing support steel that is no longer needed. The new supply air duct for the East RTU can be supported from the top angle steel (yellow on markup), but the existing steel at the bottom will not be needed (red in markup). Please advise on what steel is permissible to be removed. | Mechanical | I | 2023-10-02
Issues with Stormwater Structures Rev. 2 Please see the response from Beaty below: Beaty believe that the structures should be located no closer than 3ft clear from each other in order to facilitate compaction of backfill. Structure 15 is still closer to DIV-1 than 3ft (as is BMP-1). Would the designer accept locating STR-15 near 783204.63, 295569.88 and BMP-1 near 783210.99, 295567.75 to provide this clearance for these structures? Structure 19 appears now to be partially inside the proposed building structure, please provide clarification. Structure 18 is closer to BMP-2 than 3ft clear. Would the designer accept locating STR-18 near 783220.05, 295470.375? | Civil | III | 2023-10-07
2416 New Partition corridor office wall Clarification Due to the plywood installation on the outside of the partition A6D in the office fronts, the new partition will not align with the existing partition as shown in 1/A1. Please confirm if TSC is will be OK with a 5/8" to 3/4" difference in the corridor side where new partition meets the existing. Other option is to removed the plywood and drywall on the outside and build it as per bid set documents with plywood and R foil only on the inside, this will also eliminate the need for the frame/drywall flush condition previously discussed. | Architecture | I | 2023-10-09
Elevator 4 and 5 Divider Beam Connections to Existing CMU Walls Please reference details 1&2/A7.08 and returned shop drawing 055000-039-1: The mid-span divider beam at EL 390'-0" must connect to existing CMU wall. Detail "C" from submittal 055000-039-1 shows embed plate installed on top of CMU wall pocket. Given this CMU wall currently exists, please confirm if we are to: A.) Install embed per original design intent by removing single block, installing embed, and infill blocks below with grout until nelson studs are fully encased. B.) B.) Infill block with grout up past EL 390'-0" and then post install plate with Hilti Kwik Bolt TZ anchors. If level G1.2 slab edge exists at face of elevator 4 & 5 wall, the Hilti Kwik Bolt TZ detail from submittal 055000-039-1 should be used. | Structural | III | 2023-10-07
CDI- RFI 1 Please confirm the integral base is to be 4" high on the wall. | Architecture | II | 2023-10-08
Gateway North Leg Structural Detail Per the coordination meeting between Messer, THP, RIW, Cole Engineering and Universal Contracting on Friday 02/10/23, it was suggested that a footer detail get added to the north leg of the Gateway to eliminate any bearing connection to the Granite bench. Please provide footer details. | Structural | I | 2023-10-07
BP02 - Shear Wall Steel Install Would the steel channel framing for the shear wall in BP02 be able to be installed on the South side of the wall rather than the North side? This would ease the install from a constructability point due to all the utilities above ceiling on the North side. The impact to the hospital would also be lessened since the South side is contained in a larger construction space and more isolated from active hospital space. | Structural | Dead Reckoning | 2023-10-05
22GA Backpans at Spandrel Windows Refer to Opening Assembly Details on Drawing A0401. Please confirm use of 22GA backpans can be used at spandrel glass locations in lieu of 18GA backpans. | Architecture | Fallout | 2023-10-01
Light Fixture CL2 Clarification 1. Drawings I-231 and I-232 show cove lights tagged CL2. Multiple details on I-301 and I-401 calls for scheduled undercabinet lighting, however no undercabinet lighting is scheduled on E-604. The lighting schedule on A-060 does note CL2 as undercabinet lighting in pantry. Please confirm the CL2 light fixture is for undercabinet lighting and not cove lighting. 2. If confirmed, please confirm that the CL2 light fixture submitted in submittal 265119-001-0 is acceptable for undercabinet lighting. 3. Please provide circuitry for the CL2 fixtures at the Pantry RM 143A and at the First Floor Community Room. | Electrical | Dead Reckoning | 2023-10-03
TPO Walkway Pad Per manufacture spec we are required to install TPO Walkway pad at roof hatch entry's (3x3 area). They do not make a tan walkway mat, only grey and white are available. Are either of these colors acceptable? If so, please advise. | Architecture | Rogue Nation | 2023-10-05
Concrete Bench in Room B07.7 The drawings don't show any details for the concrete bench in room B07.7. After reviewing with Fred on site, it was determined that it would be a better idea to go with a wooden bench. Please provide details on what type of bench should be installed. | Architecture | I | 2023-10-10
RFI 286.1 - Bldg 2 Mud Mat and Footer Conflict With STM A-60 Reference is made to XXXXXXXXX. The Bldg 2 footer has been underpinned per the plan approved through RFI 286. However, the building footer and mud mat are still in conflict with the A-60 structure horizontally. Because of this, the A-60 manhole needs to be shifted 2-3' north (toward Knox Road) in order to fit. As a result, the pipe laid across Guilford Drive (between STM-50 and STM-60) will need to be re-laid and the length of pipe from STM-70 to STM-80 will need to be shortened. Please advise if this is acceptable. Also, please note that this shift means the 60" pipe will encroach, or possibly exceed, the Public Storm Drain Easement Line. Please confirm this shift will not cause the 60" pipe to go beyond that line. | Civil | Ghost Protocol | 2023-10-07
Level 2 SE Storefront Misplaced Embeds Clarification Reference EOS1.05, returned submittal 055000-011-0, and attached GPR scan photos: The embeds in bottom side of Level 3 for the Level 2 SE Storefront were misplaced due to design team comment on returned submittal 055000-011-0 (info included below). 1 dimension was mistakenly marked up, which caused a 2'0" offset East for the embeds at the SE corner. Please confirm we may proceed with post installing plates for the kicker assembly at Level 2 SE storefront. Please advise on structural provisions if necessary. GPR scan photos attached. | Structural | Ghost Protocol | 2023-10-02
Trap Primer The plumbing schedule indicates a trap primer, TP-1. The only location we see for TP-1 is in the Mechanical Room. No water lines are shown from the trap primer to any drains. However, we assume the TP-1 will serve the 3 drains in the mechanical room/fire pump room. Please confirm that is is the intent to not have trap primers connected to any other drains in the facility. | Plumbing | III | 2023-10-02
Elevator Cab Light circuits conflicting information Elevator 1,2,3,4. page LB06-E100-24 coded note 11 ask for 120v/20AMP circuit. Panel schedule for LB6-ELS-01 calls these out to be CRKT # 6,8,9,10 277V. Which is correct? Elevator 5. page LB07-E100-24 coded not 7 ask for 120v/20AMP. Panel schedule calls these out to be CRKT LB7-ELS-01 #7. 277v. Which is correct? Elevator 6. No circuits or disconnects are listed for this elevator. Please specify what cab lighting circuit and panel this should be serviced from. | Electrical | Final Reckoning | 2023-10-03
Unit D1 (Tier x06) Door Type See attached RFI from framing/drywall subcontractor and advise how to proceed. | Architecture | Dead Reckoning | 2023-10-07
HYDRONIC MAIN PIPING FOR PHASE 2A FCU'S The planned path for the hydronic mains that supply the FCU's in phase 2A will not work because they come up from the ground floor in the new north health care expansion (not yet built). For clarity please reference the attached drawing "Hydronic main piping for phase 2A". Please advise how to proceed? | Mechanical | II | 2023-10-06
Lobby Entryway Tile Spec Confirmation There is no spec provided for the tile in the lobby area outside the main entryway door to the Niskanen space. Please provide a spec for this tile as tile repairs will need to take place after main entry door modifications. | Architecture | Final Reckoning | 2023-10-09
Existing Exterior Light Fixtures Outside of Potomac Room See attached RFI concerning the existing exterior lights outside the Potomac Room and advise. See attached photo of existing fixtures. | Electrical | III | 2023-10-05
Shear Wall 2 Coupler Alternate - M&L RFI #165 Due to ongoing coordination of the mechanical opening in shear wall 2, Miller & Long expects it will need to cut the vertical reinforcing to make the reinforcing in place fit. Please confirm it's acceptable to utilize Zap Screwlok couplers to splice this interrupted reinforcing. Product data is attached for reference. | Structural | II | 2023-10-08
Roof-mounted steel finish Please confirm that the roof-mounted steel (highlighted in the attached structural drawing) for the horizontal stainless exhaust duct is to be a 2-coat epoxy paint finish. Messer suggests using a galvanized finish for durability in exposed weather conditions. | Structural | II | 2023-10-08
Bldg 1 Tyvek Detail Confirmation for the R1 Slab Edge Please confirm your approval of the section detail provided by Parksite, the Dupont Tyvek Manufacturerâ€™s rep. This warrantable detail was provided to cover the steel plate and bolts added around the R1 slab edge supporting the panel walls above. | Architecture | II | 2023-10-09
Vapor Barrier Substitution Documentation of email from Chris Bujnak for approval of 15 mil vapor barrier to replace 20 mil. 20 mil was backordered and 15 mil was in stock | Architecture | Dead Reckoning | 2023-10-03
Handicap Seating Layout Sheet A-08-201A depicts 6 wheelchair spaces at the bottom of the center section of grandstand seating. It was noted in the submitted stadium seat layout drawings (Submittal #215) that there is not enough room for 6 spaces assuming a 36" minimum spacing. On the returned submittal, it was indicated to use a minimum 30" spacing. The seating layout engineer has provided the code minimum for this scenario as being 36". (See attached reference) Please advise how to proceed and provide revised drawings of any new layout intent. | Architecture | Ghost Protocol | 2023-10-02
CMU Bracing at Auxiliary Gym Wall Please reference attached sheet A0216. Is it acceptable to brace the clouded east wall of Auxiliary Gym 1605 per detail attached? Approved detail 6/E115 from installation drawings or CMU Detail/S5302 cannot be used due to proximity of joist to CMU wall. Please advise | Structural | Fallout | 2023-10-06
Bldg 1 Courtyard Pole Shower Heat Trace Circuit Information Reference is made to Building 1 sheets A4.10, P1.14, and E1.03. Note 10 on sheet P1.14 specs heat trace on the water lines for the courtyard pole shower. Please provide circuit/panel information for this heat trace. | Electrical | Ghost Protocol | 2023-10-04
Storm Structure #6 Grade issue Storm Structure #6 has a casting elevation of 835 per the structure table C300 but the grading plan (C301) indicates the the structure in the 837 contour line. If we install Structure #6 at 835, and contour the berm around it, will we end up with a low spot the will hold water at the structure? Please confirm proper elevation of Structure #6 and nearby berm contours. | Civil | III | 2023-10-10
CCP - C Channel Color Is this C channel for the CCP supposed to be the same color as the C channel on the ED? | Architecture | Ghost Protocol | 2023-10-07
AHU Cross Member Demo Please review section of our AHU Demo plan that was approved. JDI will have crane head room issues to remove the upper cross members shown in the image. Does TKDA approve to use (2) 1-ton chain falls connected to the existing roof joist or beam to lower structural members? | Structural | III | 2023-10-08
Cedar slat clarification In referencing detail A on sheet S2.1, the detail calls for "1x/2x6". Please clarify if the intent was for 1/2" thick material or 1 1/2" thick material. | Structural | Ghost Protocol | 2023-10-09
Think Tank Perforated Wood Panels Per the millwork shop drawings, please advise on the locations of the perforations for the wood panels at the Think Tank. | Interior Design | Fallout | 2023-10-06
East FaÃ§ade Wind Girts Revised Member Reactions Please provide revised member reactions for East faÃ§ade wind girts. | Structural | I | 2023-10-10
Bathroom 1281 Interior Elevation Callout Please confirm the correct interior elevation for the South wall of Bathroom 1281 is Detail 18 located on page A-401. | Architecture | I | 2023-10-07
M103A & M105B Card Reader Please confirm Door M103A, M105B need power ran for a card reader. Drawing T101D does not indicate. This contradicts the Door hardware Schedule. | Electrical | Ghost Protocol | 2023-10-05
Light Pole Near Campus Way Relocation On sheet CE-106 there is a light pole shown to be installed right next to campus way adjacent to a gas line, see attached. This light pole is designed based on detail 8/CS502, but the gas line is currently in the way. Is it acceptable to move the light pole 5 feet to the north? Please advise. | Civil | Rogue Nation | 2023-10-03
Clean Room Egress Please confirm design intent for the egress path from inside of the clean room. Please confirm whether there are any special requirements for the HS1 doors in the event of an emergency. | Architecture | Rogue Nation | 2023-10-02
Window Wall & Metal Panel Colors The selected and approved colors for the window wall system, Eclipse Gray and Telegray II, and the specified and approved metal panel system colors, Charcoal and Pewter, are not exact matches. Please confirm these are the final selections for the two systems before material is sent to be finished. | Architecture | Final Reckoning | 2023-10-09
L03 NW U60 Doors Brick Support Due to changes in slab elevation on L03 and door sizes not reaching the underside of L04 slab, there is a space above the two U60 doors on the terrace and below the L04 slab shelf angle in which brick does not have support. Please confirm it is acceptable to use loose lintels above these doors given they are less than 8 feet wide. | Structural | Rogue Nation | 2023-10-05
Hard Lids Dimensions Level 3 Dimensions are needed for the called out gypsum board ceilings located on the 3rd floor. | Architecture | II | 2023-10-09
Wellness 1213 Backsplashes and Side splashes Note in Elevation 5/A700 indicates that countertop in Wellness 1213 is to have a 4â€ backsplash and sidesplashes, but this is not depicted in the elevation and was not shown in the reviewed solid surface or millwork shop drawings. Please confirm this backsplash and sidesplash is desired | Architecture | Final Reckoning | 2023-10-07
Steam & Condensate Flow Diagram Finalization 1/27/22: Please revise the steam and condensate flow diagram to indicate gate valves where required by UC standards. 4/1/22: Please confirm the attached PDF "RFI 493 Steam and Condensate schematic final" diagram which was finalized with UC and Pedco on 3/30/22 is acceptable. | Mechanical | Final Reckoning | 2023-10-02
Missing Piping on P1 for Level 1 Plumbing Fixtures The attached RFI from MH Mechanical shows no piping at the P1 level for plumbing fixtures located on Level 1. Please provide piping for the following fixtures: 1. Unit #104 Kitchen sink piping not shown on P1. 2. Unit #104 bathroom piping not shown on P1. 5. Community Room Sink piping not shown on P1. | Plumbing | Rogue Nation | 2023-10-08
Elec Boxes on Ladder Rack in TV Control Room 8213 Per drawing E-08-500 three circuits from UPS 2 (#21, #23, #25) are called out to be mounted at the back of ladder tray above AV Rack. There is no ladder rack called out to be installed in this room per any drawings. Please confirm if ladder rack is to be installed and/or confirm where these three receptacles are to be mounted. Note: Simple Systems confirmed on site that they do not have a use for a ladder rack in this space, nor these circuits. In addition, ladder rack would need to be mounted below ceiling, which would be a-typical for this room. | Electrical | II | 2023-10-05
Kitchen Bar Receptacle Clarification ID-160.3 is indicating a receptacle at the kitchen bar. ID-787 is showing it below the counter at 1'-6" A.F.F. and ID801.1 is indicating the receptacle to be located above the counter at 3'-3" A.F.F. This appears to be typical of the RI units with a kitchen bar. Please clarify specific location of receptacle. | Electrical | Final Reckoning | 2023-10-08
Responses to RFI 021 question Questions from RFI submitted on 6/29/2021 and returned on 7/16/2021: 1. In room C090B there is an existing Cbord panel, surface mount receptacle, power supply, hard drive and various other conduits and cables that are not shown on the electrical demo prints. Please advise if these existing items are to demo. Question 1: We are showing Room C090B as a Women'sâ€™ Restroom (a CBORD panel seems unlikely in a restroom). Please verify this is the correct room/number and we will revisit. Response 1: Yes, The Cboard panel and other items listed in this RFI are in C090B. This room was an office prior to new construction where it will become a restroom. Please advise what should be done with these items. 4. In room C090A there is a security panel mounted on the wall and a power supply plugged into a non-GFCI outlet. Please advise if these existing items are to demo. Question 4: We are showing Room C090B as a Restroom (a Security panel seems unlikely in a restroom). Please verify this is the correct room/number and we will revisit. Response 1: Yes, The security panel and other items listed in this RFI are in C090B. This room was an office prior to new construction where it will become a restroom. Please advise what should be done with these items. | Electrical | Final Reckoning | 2023-10-06
Extend NW Radius Wall Footing Radius wall footing was extended past the radius wall formwork. 3 #7 bars were drilled into existing CF1 footing. See attached file for location and picture of reinforcing steel installed. | Structural | Fallout | 2023-10-08
Overhang HHS Members Please confirm the clouded HSS members in the attachment are assumed correctly as shown in Detail 6/S5.104. | Structural | II | 2023-10-05
Exterior Snow Melt System Clarifications Reference: A-201, E-201 -Question 1: Please confirm the extent of the exterior snow melt system per the current sheet A-201, the snow melt system appears to only be shown at the south side egress ramp. However, per E-201 the snow melt system extends beyond the egress ramp to cover the egress path from stair A and the exterior Gym door. However, the egress path along the exterior patio continues from door 101B-B, which is not covered by the snow melt system currently. -Question 2: Please provide a detail or product cut sheet for installation of the snow melt system within the pedestal paver system. -Question 3: In order to provide a design/submittal for the snow melt system please provide the watts per square foot requirement. | Electrical | Ghost Protocol | 2023-10-05
Slab edge detail confirmation at C Channel piping chase Please see drawing mark-ups attached. Detail 10 on K302-S1-5-6 shows a typical slab edge detail at the service piping chase in the 2nd floor slab (K302-S1-1-243), therefore suggesting the slab to be poured over the chase and each pipe penetration to be cored and fire stopped individually within the C Channel perimeter (to maintain the slabs fire-rating). Additionally, the partitions surrounding the chase on the 2nd floor are not fire rated, which also suggests the same as above. However, detail 2 on K302-S1-5-6 calls for a large rectangular opening with "X" hashing inside the C Channel, which would void the slab's fire rating between the 1st and 2nd floors. We are assuming the slab in this location is to be poured over the C Channel Frame and each pipe penetration is to be cored and fire stopped individually. Please confirm. | Structural | I | 2023-10-02
Gypcrete on Concrete Podium Slab Clarification. Per verbal conversations between DCC & KGD on 10.12.23, please confirm that gypcrete is not required as shown on details 4 and 5 on A-452 of the contract documents, and that the flooring system assembly requires the sound attenuation mat only between the flooring material & concrete slab | Architecture | Rogue Nation | 2023-10-03
Drywall Specifications Please provide drywall specifications. | Architecture | III | 2023-10-09
Slab Edge and Column Dimensions at P2 1. The attached RFI from Miller and Long shows multiple dimensions highlighted in blue. Please confirm these are the correct dimensions at these locations, or provide an alternate dimension. | Structural | Rogue Nation | 2023-10-02
Domestic Hot Water SEHC is requesting more information about 3C when it pertains to the routing of the domestic hot water loop and how it is intended to regulate flow before returning to the main. This is important because of the meticulous balancing that has gone into the C tower itself and we don't want to repeat what happened on 6 and 7C. | Plumbing | III | 2023-10-05
Specification 08 4123 - Door 101D clarification Spec 08 4123 includes steel-framed interior sliding glass doors and sidelight panels Office (101-D). However the sliding glass door 101-D was deleted in the IFC set. Please confirm that spec (08 4123) does not apply anymore. Thank you in advance | Architecture | Rogue Nation | 2023-10-10
Theater FOH Light Rigging Please see attached drawings. TL201 shows for the front of house lighting to be 31' off the front of the stage. This lines up in the middle of the cloud ceiling and above ductwork. Please advise if suggested answer is acceptable. | Electrical | I | 2023-10-08
NW0313 and NW0327 Open Collab Ceiling Height At NW0313 and NW0327 a 7'11 1/2" ceiling height will not be heigh enough for the 8' dHive systems in that area. DCC suggests making this ceiling height 8'2" in lieu of the 7'11 1/2" called out on the drawings. Please advise if this is acceptable. If acceptable please provide a detail for the ceiling height transition. | Architecture | I | 2023-10-07
1708-4" pipe within 4" wall IN 1708 ICU WAITING room there is a 4 inch pipe partially sticking out of the 4 inch wall in room 1708 side. How should we proceed with this issue? | Plumbing | Rogue Nation | 2023-10-04
Partition Types There are a few wall types called out on A201.1 that donâ€™t appear on A601: wall types 5, 21, 23. Can you clarify? | Architecture | Fallout | 2023-10-01
Elevator Machine Beam Coordination and Penthouse Geometry Reference returned submittal 142100-002-1 and sheets EOS1.12, 15/S7.08, 4/A530, 4/A610, 4/S1.20, S7.15, 2&3/S7.10, and A7.10. 1.) Structural drawing S7.20 shows all of the beams beginning along TD line from T2 line clockwise around to just south of T3 line on TB line at elevation 577'6" and all beams are shown as 16 x 16" beams labeled 16-B02. This is shown on page 1. Page 2 on EOS1.12 shows the beams at 576'2" and 576'6". Which is correct? Please advise. 2.) On page 1, shown along TC line and from T4 to T3 line is a beam 17-B-03 which is labeled as a 35" deep beam in the beam schedule. Given the top of the high slab elevation, and top of low slab elevation plus the 9" slab, this is 36". Please confirm soffit of beam is to be soffit of low slab. 3.) At the west beam along TD line and between T1 and T2 line there is a section cut detail 15/S7.08 (page 4). This detail shows the bottom of the beam elevation 574'10". If structural elevation were correct, the beam would be 3' 4-3/4" deep. If the Arch elevation was correct it would still be 2' 8-3/4" deep. Please clarify depth of beam at this location. 4.) On the structural drawings (page 1), there is a CMU screen wall shown in plan along west side of building from T2 north and then east to TC and then returns to the south. The remainder of the beams have a section cut through them 13/S7.08 which shows 16" x 16" beam with CMU parapet wall on it. When you follow the elevation 1/A4.02 (see page 5) you end up with only a section cut 4/A5.30 which is showing the 8" concrete curb. The east elevation does not cut a section through the area just south of T3 line to the north end of the building. Please confirm that structural drawings are correct and that this is a CMU parapet wall as shown. 5.) The high roof above elevators has a low point elevation of 580'9" and a percent slope up shown only. When scaling this in all directions it amounts to +4" so the elevation at high point will be 581'1". Please confirm this elevation as it dictates the height of the bands above the south end of the machine beams. 6.) There are some openings shown on EOS1.11 and EOS1.12 that do not have curbs around them. Please confirm concrete curbs are not required at those openings. 7.) On detail 3/S7.10 (page 9), at the north side of elevators 1, 2, and 3, there are 6 pockets for the machine beams. Please confirm that it is acceptable to leave the remainder of the wall boxed out to the soffit of the slab above to allow the machine beams to be set with crane prior to pouring the roof over the top of the machine beams. 8.) On returned submittal 142100-002-1, given the 16'2" dimension to the bottom of the machine beams that are 12" deep, the clearance between the top of the machine beams will vary. At the high point, it will be 1' 8-7/8" to as low as 1/5". Please confirm this is correct. 9.) Regarding question 8 above, for elevators 1-4, there could be a need to install metal deck as M&L will require a minimum of 12" clear to frame over the equipment. Note that this is only allowing about 4 additional to strip the material. Please clarify if metal deck will be installed over all 4 elevators. | Structural | Dead Reckoning | 2023-10-08
Service Well 1139 Door Looking at the food service print FS2-1.0 there is a door shown at the entrance to the service well. On the Arch and ID drawings there is not one shown. Please advise if this door is needed. Also, I have clouded the south wall of the entrance to the service well because there is duct that passes directly over it and will keep it from topping out. Is it acceptable to not top this wall out? | Architecture | Dead Reckoning | 2023-10-07
BP01 - Humidifier What is the minimum distance we can be from the humidifier? See attached. | Mechanical | Dead Reckoning | 2023-10-06
OR 5 Doors OR 5 Door (Now referred to as 2-A057) was previously approved by the Owner. See attached submittal from what was previously approved. Note that the height of the door was previously approved for 7'10" in lieu of what the OR 7, 5, and Lounge project shows 8'0". Please review previously approved submittal and verify this is still acceptable. Note: The door and frame for OR 5 was already purchased and currently ready to install. | Architecture | I | 2023-10-02
2 PANEL DOORS Please see attached question and related information on doors that were rejected | Architecture | Final Reckoning | 2023-10-10
X-03 Bathroom Doors Please advise if it is acceptable for the X-03 bathroom doors to be right hand outswinging as shown in the attached mark-up, in lieu of right hand inswinging as shown on the contract drawings. This would eliminate the need to furnish new doors. | Architecture | Final Reckoning | 2023-10-06
Load at Column On drawing S1.04B Column Line AA; 22-23 shows a steel beam going across the storefront. The concern at this location is the CMU column not having the load capacity to support the W18X35 beam which is 28 feet wide and the two HSS beams going across the opening. The ask is if we can put a CMU column at the corner of the W18X35 to have more support at this location? Or add a 4 feet column that is highlighted blue on the drawing this will be extended from the second level if CMU column if this option was selected. | Structural | Fallout | 2023-10-02
Lower Level Wall Layout Walk "Please see attached lower level wall plan marked up to reflect changes discussed during the 11/30/22 site walk between Perkins & Will, Akelius and DCC for your confirmation of architect approval of wall layout." | Architecture | III | 2023-10-01
Makeup Air for Fire Place Exhaust Reference M1.03 and M1.04: Please confirm OAHU-2M-1 has enough air to cover he makeup air required for the Level 1 and 2 fireplaces. Please update sheets accordingly. | Mechanical | III | 2023-10-09
Building 2 Trash Room - Power to Overhead Door Reference is made to Detail 3/A3.53. The contract documents specify the overhead door in the Building 2 Trash Room to be operated manually with a chain fall. However, the specified door comes with a motor and is only designed to be operated manually in emergencies only. A wire has already been run to the motor. Please advise which panel/circuit this wire should be tied into. | Electrical | Rogue Nation | 2023-10-10
Unit Storage Carrier Wall Water closet carrier in the unit storage doesn't fit in the 6" stud wall. | Plumbing | Final Reckoning | 2023-10-04
Headwall Differences Drawing 2-A9.4, doesn't show the electrical outlet behind the bed and the data behind the screen as shown on drawing 2-E3.3 (2) typical patient headwall. What drawing do we rough-in for? | Electrical | Dead Reckoning | 2023-10-05
PL-501 in Cigar Bar 76/ID 9.24 and 77/ID 9.24 call out plastic laminate PL-501 for a small section of casework in the Cigar Bar. There is no color selection for this anywhere in the architectural drawings and we failed to include it in our submittal. It snuck completely through the process. Please advise on color selection. | Interior Design | Final Reckoning | 2023-10-02
CONFIRMING - Hardy Trim Parapet Wall Panel and Break Metal Under Window This is a two part confirming RFI that was discussed on 5.16.23 Site walk. Part 1: Please confirm that Fiber cement panel shown on A616 Detail 1 for balcony roof parapet wall is to be 9.5" hardy trim board, light mist color to match the siding panel that's in the courtyard. Part 2: Please confirm that break metal can be used to cover exposed roof under windows. The terrace windows are 4 inches above the slab and the drawings call for roof tern bar to be installed 1ft 6 inches over roof putting it 12 inches over finish floor and pavers. This is where the siding will start leaving exposed roof under windows. | Architecture | Ghost Protocol | 2023-10-01
compressed air tie in location Can we tie in the compressed air on the 3rd floor tech space 25-306. There is an abandoned 1-1/2" line with a valve and a plug. To tie into the compressed air in the tech space, we will have to shut down half of the plant. If we use the 1-1/2" line, no shut down is necessary. We will tie into the 1-1/2" valve and head west down the wall, then go down through floor into Zanchetta chase, then following the route on the drawing from there. | Mechanical | Fallout | 2023-10-09
Cafeteria Terrace Paver Low ACM Band Refer to the attachment. During a site walk on 12/21/22 with Messer, Hastings and NRC it was agreed that due to the actual opening size (~3") from top of paver to bottom of window, that the MP1 should be replaced with a brake metal assembly similar to the MC3 sill/wall panel on the interior side of A4.14B/7. Since the window is already installed, it was discussed that this brake metal would need to be coordinated with the windows primary dry-line seal on the exterior. If there is a certain detail desired for this condition please provide. | Architecture | Dead Reckoning | 2023-10-09
Confirm Storm Demo Note Please confirm this plan note is tied to the SD line directly to the south and not an additional storm line not shown on the drawings. | Civil | I | 2023-10-04
Handhole Boxes Their are 3 handholes located at the SE corner of the hospital. These will be located within the footprint of the new building and will potentially be in conflict with a pile cap. The electrical contractor has removed most of the abandoned and unneeded wires. Several conduits remain in these handholes (attached PDF will show you location and other information) and need to be refed. Presumably some of these will need to remain active through the project. Please advice on what needs to be done with the remaining. | Electrical | II | 2023-10-05
Exhaust Fan 110 Confirming RFI Per our conversation with Jason Smith while on site, a velocity stack is not needed for EF-110 since there are no longer fume hoods in the lab space. There is a drain in the bottom of the exhaust fan housing for water that occurs on the roof. The exhaust fan will be capped with a bird screen. | Mechanical | Fallout | 2023-10-01
Recessed Toilet Paper Dispenser Sheet A.432.7 shows toilet details with both recessed and non-recessed toilet paper dispensers. Please clarify if all toilet paper dispensers are recessed. If not, please specify which bathroom get recessed toilet paper dispensers and which do not get recessed toilet paper dispensers. | Architecture | Ghost Protocol | 2023-10-02
Dining Room Chandeliers There are (8) existing chandelier light fixtures called out to be cleaned, rewired, and provide new LED lamps within each of the (16) base lamps. While inspecting the light fixtures, Electric Plus also noticed some sockets are loose, and they recommend the replacement of the sockets. Please advise if we should add replacing the sockets to their light fixtures. Also, to ensure expectations are aligned we will be providing a wipe down clean of the fixtures per the note, and the pitted look of the brass will remain. This will leave the old, historic look. Please advise if the wipe down clean is sufficient, or if a full polish and restoration should be added to the scope. | Electrical | III | 2023-10-04
Normal & Emergency Feeders @Fire Pump Discrepancy Ref: E700, 013100-02 Refer to attached RFI - There's a review comment within the Electrical Underground Composite Drawings submitted under 013100-02 on page UG-L1-1E , that directs B&D to provide (2) 2.5" conduits from both "MSWB" and & "GEN". This direction directly conflicts with the scheduled conduit size provided on E700 where Normal power ("B" - MSWB) is called out as 1.25" conduit and Emergency power ("AS" - GEN) is called out as 1" conduit. Please confirm if Bausum & Duckett is to provide conduit sizing at the referenced locations per the mark-ups provided on submittal 0131000-02. | Electrical | Final Reckoning | 2023-10-10
Door S05A - Clarification Reference: CCD-005, 1/A5.07 CCD-005 moved this door south. In order this door to be 89 3/8" x 110 Â½" (Each leaf width 44 5/8") will require a 5" Top Rail instead of the standard Medium Stil 3 Â½" top rail per EFCO's door size requirement sheet. Based on the chart the max width of door would 86-1/4" with each leaf to be max 43" in order to retain the 3-1/2 top rail as all other doors on the project. Please confirm which direction to follow. If shrinking door opening to 86-1/4" to retain the 3-1/2" top rail SF4(W34B) would have to have an RO of 93-1/4". (See attached) | Architecture | I | 2023-10-09
Facade Transition at South Elevator Overrun Please provide a transition detail for the south faÃ§ade of the penthouse metal panels to the elevator overrun Tnemec coating. The penthouse level is ACM metal panels at the VRV mechanical well and 5/A308 indicates a transition and termination from ACM to the Tnemec coating at the elevator overrun. | Architecture | Rogue Nation | 2023-10-05
DIMENSION BUST ON SHEET A101 IN ROOM 101H STAGING THE TOTAL WIDTH OF THE ROOM IS 295" NOT ALLOWING THE 312" NEEDED FOR THE 6 REFRIGERATORS SHOWN . PLEASE ADVISE | Architecture | Final Reckoning | 2023-10-08
Kitchen Wall Outlets The kitchens in Units X-01, X-04, X-05, and X-06 have block walls where cabinets/countertops are to be installed, so wall outlets are not feasible. Please advise how to install the outlets above the countertops in these units. | Electrical | Ghost Protocol | 2023-10-03
Fan Coil Unit Fan Status Alarm Is FCU failure to be alarmed on the BAS? BR+A reports this was done at RB4 but does not call for it on the LOSC project. This is related to a submittal review of the 230993 SOO specifications. | Mechanical | III | 2023-10-09
Mesh Reinforcing The structural drawing calls out mesh that encompasses the east office space. Please confirm weather or not this is necessary. In addition, should mesh reinforcing be extended due to the loads associated with the overhead door? See the attached document. | Structural | II | 2023-10-07
Test RFI Restroom 197: toilet specified doesn't meet ADA requirements, please confirm if this matches design intent | Architecture | II | 2023-10-08
Wood Base Locations See attached plan markups 1. Please confirm the DIRTT contractor will install scheduled wall base on DIRTT panel walls 2. Sheet A-9.1 shows Room 0102C is scheduled to receive rubber base with the adjacent Room 0118 while the other Help Desk areas are scheduled for wood base. Please confirm which is desired in Room 0102C | Architecture | Final Reckoning | 2023-10-08
Closet Carrier Conflict Chase walls in bathrooms areas arenâ€™t thick enough to accept the depth required for Water Closet Carriers. Single closet carriers require a 11.5â€ depth. Double closet carriers require 15.5â€ depth. Please advise how to proceed with new wall dimensions. See attached file (Chase walls in conflict are highlighted in yellow) | Plumbing | Fallout | 2023-10-02
Winterization Drain : Elevations The winterization drains for the baseball and football concession buildings require RIM and invert Elevations to be provided. Please advise. | Civil | I | 2023-10-01
Escalator W16 Beam This W16 beam needs to slide to the right 5" with the escalator opening similar to RFI 33 sliding 9" to avoid the girder on the north. When we do this, there will only be about 5" of slab overhanging the concrete girder. Given the minimal overhang, can this beam be eliminated? Note, this beam was in place prior to the RFI 33 response and opening size finalized. | Structural | Ghost Protocol | 2023-10-08
G581 Female Staff Toilet - Sink & Toilet Clarification RFI Due Date 3/29/23. Per drawings P0100B.4 & P0100C.4, the sinks are called out to be B1 fixtures and the toilets are called out to be A1 fixtures. Per drawing P0200B.4, the sinks are called out to be B3 fixtures and the toilets are called out to be A2 fixtures. Per drawing P0200C.4, the sinks are called out to be B1 fixtures and the toilets are called out to be A2 fixtures. Which fixtures are correct for G581 Female Staff Toilet? Please make sure all drawing sheets reflect the same fixtures. | Plumbing | Rogue Nation | 2023-10-08
Entry hallway - touch up walls Touch up walls where green tape is. | Architecture | Fallout | 2023-10-05
Work to Complete Missing window hoist tie on hold | Architecture | II | 2023-10-08
Bedroom closet - install doors Install closet doors. | Architecture | I | 2023-10-10
Coordination SSK01 NOTE B ADD 2X6 UNDER TRUSS FIX 2X6 TO THE LEFT | Structural | I | 2023-10-08
Door Damage Canâ€™t enter the room | Architecture | I | 2023-10-04
Safety FDC Pipe needs to be extended up. So far it has been run up to second floor. | Fire Protection | Rogue Nation | 2023-10-07
Punch List Unit 905 - refrigerator leaking. Appears to be issue with ice maker | Mechanical | Fallout | 2023-10-07
Coordination SSK01 Add 2 2x4s Move stud over right under joist | Structural | Rogue Nation | 2023-10-01
Living room- touch up wall Touch up wall where green tape is. | Architecture | Fallout | 2023-10-10
Window Screen Just to note this window screen is secured in place with screws | Architecture | Dead Reckoning | 2023-10-02
Owner Punch List Unit 204 - locked door on laundry closet, need door without a lock | Architecture | Ghost Protocol | 2023-10-05
Sprinkler Escutcheon Missing | Fire Protection | Fallout | 2023-10-03
Work to Complete Pipes out of wall | Plumbing | III | 2023-10-07
Work to Complete Duct modification in Church Egress | Mechanical | Dead Reckoning | 2023-10-07
Punch List unit 402 - front door deadbolt and strike plate misaligned | Architecture | Fallout | 2023-10-05
Bedroom-Closet Door - Clean door hinge Discoloration at hinge | Architecture | Ghost Protocol | 2023-10-07
Quality Hoist room fully saturated due to intrusion from rain. North Exterior wall of hoist room not yet hung. Remove bottom 2â€™ of drywall at exteriors to monitor and dry out. Do not rehang until envelope is complete at hoist. | Architecture | Fallout | 2023-10-08
Bedroom closet - touch up wall Touch up wall inside closet. | Architecture | Dead Reckoning | 2023-10-04
Brightview Warranty Issue Template Error code E202 was reported to AMSI. AMSI mobilized to investigate and found a compressor to be bad, as well as inverter needing replacement. Currently being processed under warranty, ETA on parts is TBD, working with AMSI to get this information | Mechanical | III | 2023-10-03
Trash room Fire caulk all electrical. | Fire Protection | I | 2023-10-09
Ceiling Grid Paint Ceiling grid is damaged and needs touchup paint | Architecture | Fallout | 2023-10-05
ARIS Work to Complete Grout F1 Fireplace | Architecture | III | 2023-10-05
Den - touch up trim Touch up trim. | Architecture | Ghost Protocol | 2023-10-09
KTEF-1 Fan Summit Site Visit 10/10/23: Exhaust fan KTEF-1 is not installed. Please assure this installation does not obstruct discharge of any VRF outdoor units. | Mechanical | Ghost Protocol | 2023-10-03
Work to Complete threshold missing | Architecture | Rogue Nation | 2023-10-05
Sanitary pipes leaking at Retail Area Check and fix the Leak for the sanitary pipes near CMU wall on Gridline G, Southeast Retail Area. | Plumbing | Dead Reckoning | 2023-10-08
Living room - remove extra pieces of trim Remove extra piece of trim. | Architecture | III | 2023-10-03
Bathroom 2 - caulk sides of medicine cabinet Caulk both sides of medicine cabinet. | Architecture | III | 2023-10-08
Add missing coat hook on door Add missing coat hook on door | Architecture | Final Reckoning | 2023-10-05
Touch-Up Paint FCU | Mechanical | Final Reckoning | 2023-10-10
Touch-Up Paint Corridor side | Architecture | Final Reckoning | 2023-10-06
Bathroom - Lower Mirror Drop down bathroom mirrors so bottom of mirror is no higher than 40" AFF. | Architecture | Fallout | 2023-10-04
CHS Work to Complete complete base boards | Architecture | Final Reckoning | 2023-10-09
Work to Complete threshold missing | Architecture | Final Reckoning | 2023-10-06
South Sink Hall - J6 J6 not rough in. Need rough-in | Plumbing | Fallout | 2023-10-10
Punch List Unit 301 - paint/caulk trim by bedroom B | Architecture | Ghost Protocol | 2023-10-07
Safety Level 2; guard rails to the left of hoist not set correctly, guard rails must be installed at 42â€ and 21â€ plus or minus 3â€. Level 4 northeast; top rail was missing. Not sure whoâ€™s responsible. | Structural | Final Reckoning | 2023-10-05
Sprinkler Escutcheon Missing | Fire Protection | Dead Reckoning | 2023-10-07
Entry hallway - touch up walls Touch up walls. | Architecture | I | 2023-10-10
Penthouse Outdoor VRF Unit Piping Summit Site Visit 10/10/23: During coordination it was discussed to run VRF piping under the bank of 6 outdoor units on the south side of the building to allow more access around the units. During site visit, Summit noted that sold support curbs were used, and piping was routed behind the units obstructing access options from the inside pathway (closest to the building). | Mechanical | II | 2023-10-04
Touch-Up Paint Touch-up paint throughout room | Architecture | Ghost Protocol | 2023-10-04
Master bathroom - touch up wall Touch up walls where green tape is. | Architecture | Final Reckoning | 2023-10-02
Punch List Unit 501 - bathroom E sink drain won't open | Plumbing | Final Reckoning | 2023-10-07
Owner Punch List Unit 203 - paint sides of window sills | Architecture | Ghost Protocol | 2023-10-10
Sprinkler Escutcheon Needs to be fixed | Fire Protection | Dead Reckoning | 2023-10-04
Congressional - Vertical Elevator Entrance Support Provide vertical support in the elevator lobby entrance. | Structural | Dead Reckoning | 2023-10-02
Work to Complete Missing schlutter | Architecture | Ghost Protocol | 2023-10-03
Owner Punchlist - Clean cast stone Clean stains off of cast stone | Architecture | III | 2023-10-08
Coat closet - missing bracket? Missing bracket? | Architecture | Ghost Protocol | 2023-10-02
Entry hallway - touch up walls Touch up walls. | Architecture | Final Reckoning | 2023-10-04
Kitchen - clean garbage disposal Clean garbage disposal. | Plumbing | II | 2023-10-07
Ceiling Grid Paint Damaged grid removed from ceiling | Architecture | Fallout | 2023-10-10
Quality Water in wall track unknown cause. Probably temp wp at parapet. | Architecture | I | 2023-10-05
Complete FCU Survey Complete FCU Survey. Room occupy the time of survey at end of project no issues found | Mechanical | Ghost Protocol | 2023-10-10
Coordination Kitchen add top plate strapping | Structural | Rogue Nation | 2023-10-10
Entry hallway - touch up walls Touch up walls. | Architecture | Fallout | 2023-10-07
Safety Level 14 ; receptacle box hanging from the the wire, it was probably dismounted when framing was done. Maintenance required | Electrical | Rogue Nation | 2023-10-07
Punch List Unit 405 - point/touch up all windows, door casing and bases see blue tape | Architecture | Ghost Protocol | 2023-10-01
Entry hallway - touch up walls Touch up walls. | Architecture | Dead Reckoning | 2023-10-10
Beco Work to Complete install F/A devices | Fire Protection | III | 2023-10-04
Living room - seam in ceiling Seam in ceiling. | Architecture | Rogue Nation | 2023-10-10
Steven Winter Associates Water Closet: Location. The centerline of the water closet is 18Â½ inches, measured to the side wall. A distance of 16-18 inches must be provided. | Plumbing | Ghost Protocol | 2023-10-05
Observation Light fixtures out in some stair landings | Electrical | Dead Reckoning | 2023-10-02
Work to Complete Camera conduit at roof | Communications | I | 2023-10-07
Kitchen - pencil marks on drawers Pencil marks inside drawers. | Interior Design | Rogue Nation | 2023-10-07
b. Work to Complete Install faucet and supply lines | Plumbing | Ghost Protocol | 2023-10-04
Coordination Kitchen add top plate strapping Bathroom add 2 studs under truss | Structural | II | 2023-10-02
Door Damage Door has a gouge in it | Architecture | Dead Reckoning | 2023-10-02
BECO work to complete install light in closet | Electrical | Final Reckoning | 2023-10-04
Work to Complete Calking bathroom and kitchen | Architecture | II | 2023-10-05
Punch List Unit 205 - caulk granite to wall in kitchen | Architecture | Fallout | 2023-10-04
Master bedroom closet - install light fixture Light fixture not installed. | Electrical | I | 2023-10-06
Laundry closet - touch up door frame Touch up door and door frame. | Architecture | II | 2023-10-04
Entry hallway - touch up walls Touch up walls where green tape is. | Architecture | Ghost Protocol | 2023-10-01
Punch List Unit 203 - remove paint on grill | Architecture | Ghost Protocol | 2023-10-07
Bathroom/closet door - Touch up paint Touch up paint. | Architecture | III | 2023-10-09
Coordination Kitchen add SSK03 and add 4 studs Bathroom add top plate strapping and add stud | Structural | II | 2023-10-01
Work to Complete Finish point up | Architecture | Dead Reckoning | 2023-10-07
Punch List Alpolic Panel missing support at bottom/clean panel,bottom flashing | Architecture | Rogue Nation | 2023-10-08
Brightview Warranty Issue Template Entrance parking garage gate not closing | Electrical | I | 2023-10-04
BECO Work to Complete MISSING TRIM | Architecture | Dead Reckoning | 2023-10-05
Pantry closet - touch up paint door Touch up pantry door and frame. | Architecture | Dead Reckoning | 2023-10-08
Punch List Unit 401 - seal bottoms of all doors | Architecture | Final Reckoning | 2023-10-02
Steven Winter Associates Lavatory: Mirror. A mirror was not installed at the time of inspection. | Interior Design | Final Reckoning | 2023-10-09
Punch List Unit 505 - caulk granite to wall in kitchen | Architecture | Fallout | 2023-10-03
Work to Complete Back box needs to be installed at limestone | Electrical | II | 2023-10-09
Observation Align GWB bulkhead with ACT ceiling. | Architecture | II | 2023-10-10
b. Work to Complete Unit 404 - patch by sprinkler needed | Fire Protection | III | 2023-10-09
Coordination Kitchen add top plate strapping Bathroom/corridor add top plate strapping on both sides | Structural | Ghost Protocol | 2023-10-05
Coordination Kitchen add top plate strapping Bathroom/Corridor add top plate strapping | Structural | Final Reckoning | 2023-10-01
Pre-hung doors & frames - scratches/kinks/dents Fix scratches, kinks, and dents at all doors and frames. | Architecture | Dead Reckoning | 2023-10-08
Fill in screw heads at interior header door 319b Fill in and paint screw heads at the header on the interior side of side of door 319b | Architecture | Fallout | 2023-10-06
Living room - touch up walls Touch up walls. | Architecture | Ghost Protocol | 2023-10-09
Hallway - fix seam in wall Fix seam in wall. | Architecture | Rogue Nation | 2023-10-03
Bedroom - touch up walls Touch up walls where green tape is. | Architecture | Fallout | 2023-10-06
Metro Work to Complete Paint Ceilings and walls | Architecture | I | 2023-10-03
Bathroom - inconsistent caulk fix caulk at side of shower | Plumbing | Rogue Nation | 2023-10-04
Work to Complete Insulate waterline f1 South side at main entrance | Plumbing | Final Reckoning | 2023-10-06
Mechanical closet - touch up walls Touch up walls. | Architecture | I | 2023-10-04
Work to Complete Calk kitchen and bathroom sink | Plumbing | Rogue Nation | 2023-10-10
Work to Complete please adjust your pipes Pipe is stopping drywall work | Plumbing | Ghost Protocol | 2023-10-05
Work to Complete Missing window | Architecture | Rogue Nation | 2023-10-03
Owner Punch List Unit 902 - unit touch up needed/paint removal. See blue tape | Architecture | II | 2023-10-06
Coat closet - touch up doors Touch up door. | Architecture | Rogue Nation | 2023-10-09
Window Screen Stair two side window screen corner ripped | Architecture | Final Reckoning | 2023-10-08
Bathroom 2 - scratches on the tub Scratches/scuffs on bathtub. | Plumbing | Dead Reckoning | 2023-10-10
Work to Complete Need fire rated glass window | Fire Protection | Rogue Nation | 2023-10-08
Congressional - PL#18 Angle not installed | Structural | Dead Reckoning | 2023-10-01
NDC Work to Complete FINISH POINT UP | Architecture | Fallout | 2023-10-10
Entry hallway - touch up walls Touch up walls. | Architecture | Rogue Nation | 2023-10-10
Quality Visible water below wall between windows. Marked drywall for removal | Architecture | Final Reckoning | 2023-10-06
Punch List Unit 205 - seal bottoms of all doors | Architecture | III | 2023-10-10
Living room - touch up trim Touch up trim. | Architecture | Ghost Protocol | 2023-10-06
Expansion Joint at main roof Screen wall is not completed. complete expansion joint north screen wall @ gridline 12, Main Roof. | Structural | Ghost Protocol | 2023-10-05
POINT UP Get rid of white chunk | Architecture | Ghost Protocol | 2023-10-08
Kitchen - Outlets not working Outlets not working at kitchen. | Electrical | I | 2023-10-10
Sprinkler Escutcheon Both missing | Fire Protection | Fallout | 2023-10-04
Master bedroom closet - touch up walls Touch up walls where green tape is. | Architecture | III | 2023-10-10
Entry hallway - touch up walls Touch up walls where green tape is. | Architecture | Dead Reckoning | 2023-10-10
Bathroom - caulk side of medicine cabinet Caulk side of medicine cabinet. | Architecture | III | 2023-10-07
Door doesnâ€™t auto close Thereâ€™s not a spring hinge present | Architecture | Ghost Protocol | 2023-10-05
Install missing bathroom strikes Awaiting materials | Architecture | Final Reckoning | 2023-10-05
Punched stud at sill of windows opening There is a window opening on the third floor, East elevation that has a knock out stud in the sill. Needs to be changed to a solid stud. | Structural | Fallout | 2023-10-02
Kitchen - touch up cabinets Touch up cabinets. | Architecture | Fallout | 2023-10-04
Millwork Damage Left 2nd down drawer and right 1st and 3rd down drawer does not open easily. Gap at bottom shelf area in between interior area and back board. Braces in both closets do not match stain. Damages found at both closet door sets. | Interior Design | III | 2023-10-08
Heat Trace Install Issue on Cooling Tower Piping Heat trace is not installed per Raychemâ€™s literature. HT to be installed on bottom 45 of pipe. | Mechanical | I | 2023-10-10
Tile uneven tile/grout lines | Architecture | II | 2023-10-08
Improper Piping Storage Piping is stored directly on slab, should be stored up off the slab on cribbing with chocks. Pipe ends should be covered in stored locations. | Plumbing | I | 2023-10-07
Warranty Paint soffit | Architecture | III | 2023-10-03
Paint / Wall Repair Tile edge | Architecture | III | 2023-10-10
Punch List Install blank cover | Electrical | III | 2023-10-02
Pre-Punch List Light fixture not working In cloud | Electrical | Fallout | 2023-10-02
Patch fireproofing In-wall Patch fireproofing | Fire Protection | Ghost Protocol | 2023-10-02
Punch List Fire caulk penetration | Fire Protection | Ghost Protocol | 2023-10-01
East Parking Lot Punchlist Scratch in curb | Civil | I | 2023-10-06
Safety Fire extinguishers need to be up off the ground when stored. | Fire Protection | I | 2023-10-05
Drywall Patch and Paint in corner Please patch to ready for paint | Architecture | Ghost Protocol | 2023-10-04
Remove paint bridging at FCU. Remove paint bridging at FCU. | Mechanical | I | 2023-10-08
Punch List Install screws in stops | Architecture | Ghost Protocol | 2023-10-10
Punch List . Touch up paint. | Architecture | Rogue Nation | 2023-10-06
4B SCA Final Punch Rough edge and nail around baseboard | Architecture | II | 2023-10-07
Punch List Tighten sprinkler cover vitals area. | Fire Protection | Ghost Protocol | 2023-10-04
Damaged Coil HHW connection to coil of VAV V15-58 has been damaged and coil needs replaced. | Mechanical | Fallout | 2023-10-04
Receptacle Box Needs Cover Plate Receptacle Box Needs Cover Plate | Electrical | Rogue Nation | 2023-10-03
SCHILLER Install card reader CR.01.31 | Communications | I | 2023-10-04
Quality - Site Signage Crosswalk sign on southeast corner of 4th and Market. sign on ground and sand bag busted open. | Civil | I | 2023-10-08
Clash South perimeter wall 126 around overhead doors - no detail given on it. May need to have possible adjustment of framing studs for OH Door tracks being mounted directly to brick. | Architecture | III | 2023-10-04
Messer Punch List Sprinkler heads not centered In | Fire Protection | Dead Reckoning | 2023-10-06
Quality Cove ahu | Mechanical | Fallout | 2023-10-10
Fix flashing South end of area D, jamb flashings are different from opening to opening | Architecture | Final Reckoning | 2023-10-03
Pre-Punch List Repair tile at rear of pulmonary side at rear of suite | Architecture | I | 2023-10-07
Safety Fire extinguisher in Messer skid steer needs replaced | Fire Protection | II | 2023-10-10
Documentation of Existing Pressurization - 6th floor at West Stairwell 0â€ w.c. | Mechanical | I | 2023-10-03
Pre-Punch List Removed blue plastic from grill | Architecture | Ghost Protocol | 2023-10-09
Plumbing Kitchen sink only got to 109 degrees after 20 minutes (William Tested after 5 minutes 116Â° CLOSED 9/20/22) | Plumbing | Rogue Nation | 2023-10-10
Light not working Light not working | Electrical | II | 2023-10-07
Temporary Wires Temporary wire needs to be pulled before it can be patched. | Electrical | Final Reckoning | 2023-10-07
Quality Line A3 building D2 anchor bolts are 0.25 inches off. | Structural | III | 2023-10-10
Safety Elevator form break is 23â€ in elevation change. Step was added . | Architecture | III | 2023-10-05
Punch List #26: 30" x 12' old conduit chase w/ curb | Electrical | Ghost Protocol | 2023-10-01
Quality Additional reinforcement around stairwell | Structural | Fallout | 2023-10-04
Quality Wrong trim was installed at end wall and overhead door base. Fix is pending EAT delivery of new ash Grey base trim | Architecture | II | 2023-10-03
Pre-Punch List Touch up paint on window frame | Architecture | I | 2023-10-05
Fire damper door access Unable to open access door. Adjust drywall per ERI-M directions | Architecture | I | 2023-10-08
Punch List Correct base | Architecture | I | 2023-10-03
Trim Install Install trim at wood paneling/ceramic wall tile transition. | Architecture | II | 2023-10-03
Existing Condition Demo? | no | III | 2023-10-05
Punch Locked, not reviewed | no | Final Reckoning | 2023-10-08
Punch List Install caulk ilo grout | Architecture | Rogue Nation | 2023-10-01
Quality Extra core hole needs to be fire stopped or grouted. | Fire Protection | Fallout | 2023-10-09
Quality 2 cap bars missing at JBN 108 beam end @ intersection with FBN 261. | Structural | III | 2023-10-09
Pre-Punch List Paint doors | Architecture | Rogue Nation | 2023-10-09
Temp lighting No temp lighting in northeast stair from street to ground level. | Electrical | Fallout | 2023-10-09
Quality Move mc cable from touching sprinkler line | Electrical | Rogue Nation | 2023-10-07
Door Switch causes door to pop open | Electrical | I | 2023-10-06
SME Whips touching sprinkler | Fire Protection | Final Reckoning | 2023-10-05
Punch List - 6th Floor Unit D shower caulk | Plumbing | Rogue Nation | 2023-10-10
confirm EA duct is installed. extend duct to grille. Confirm EA duct is installed. | Mechanical | III | 2023-10-06
Above Ceiling Issue Patch hole in drywall | Architecture | Rogue Nation | 2023-10-02
Doctor's Office - Messer PL Install closet rod | Architecture | III | 2023-10-06
Repair drywall Repair drywall | Architecture | I | 2023-10-01
Precast Panel #1041 (4) There is a chip in top left and top right corner and a chip in the middle of the left side. | Architecture | Rogue Nation | 2023-10-05
Warranty Shower leakage to bathroom below | Plumbing | Rogue Nation | 2023-10-02
Punch List Touch up paint at dorm room door frames along hallway at blue tape | Architecture | Ghost Protocol | 2023-10-06
Caulk Wall Protection Caulk wall protection | Architecture | Final Reckoning | 2023-10-03
Fix insulation Above ceiling- fix insulation on duct | Mechanical | I | 2023-10-06
Pre-Punch List Tape and caulk above duct grill (neatly) | Mechanical | Final Reckoning | 2023-10-10
SF2 South C111 Center Glass, clean excess Butyl, fix gaskets | Architecture | Rogue Nation | 2023-10-04
Is Strainer is backwards on return to RHC Is Strainer is backwards on return to RHC | Mechanical | III | 2023-10-03
Work to Complete No rough-in | no | Rogue Nation | 2023-10-08
Punch List - 2nd Floor Unit F Paint Touch Up | Architecture | Ghost Protocol | 2023-10-08
Pre-Punch List Install access panels after partial occ | Architecture | Dead Reckoning | 2023-10-03
Pre-Punch List Cut in light | Electrical | Rogue Nation | 2023-10-04
L3C/D Punchlist - Valley Touch up drywall at green tape. Leave tape on wall | Architecture | Rogue Nation | 2023-10-07
Pre-Punch List removing pipe brackets in wall backing | Plumbing | Rogue Nation | 2023-10-10
Majestic Range strip in kitchen | Architecture | Rogue Nation | 2023-10-06
Punch List 31 Valley- repair dents dings and damaged drywall, inspect and repair all ceiling tile. Each room has at least one issue needing addressed. Non factory edges must be painted Stithmeier- Follow behind and paint all repairs made by valley. All rooms have unfinished or damaged paint by the bulkheads and shade pockets. | Architecture | Ghost Protocol | 2023-10-03
Remove temporary electric Remove temporary electric from exterior wall in group study 3062. Fire stopping will need patched | Electrical | Rogue Nation | 2023-10-06
Not reviewed; locked Not reviewed; locked | no | Ghost Protocol | 2023-10-09
RFI-384 Please provide detail and locations for the 4 typical bollards indicated in the dumpster pad per sheet CL102. | Civil | Final Reckoning | 2023-10-07
Messer Punch List Patch and paint window sill | Architecture | Dead Reckoning | 2023-10-03
Light needs to move Currently in the way of forks on crane. | Electrical | Rogue Nation | 2023-10-05
Quality Drilled Shaft 9 | Structural | III | 2023-10-10
Touch up paint Touch up paint | Architecture | III | 2023-10-10
Door Frame Paint Touch Up The door frame needs a paint touch up | Architecture | III | 2023-10-03
Door blocking Blocking required for door 1020B | Architecture | Final Reckoning | 2023-10-10
Firestop penetration Firestop penetration | Fire Protection | Fallout | 2023-10-05
Punch List Remove paint | Architecture | Dead Reckoning | 2023-10-01
Messer Punch List Touch up and paint needed | Architecture | Rogue Nation | 2023-10-05
P1.2 Negative Air Sign off Negative air sign off was incomplete morning of the 14th. | Mechanical | Fallout | 2023-10-01
Remove paint bridging Remove paint bridging | Architecture | Rogue Nation | 2023-10-03
Punch List Sconce not installed, typical throughout on floor 3 | Electrical | Rogue Nation | 2023-10-09
Touch up paint Touch up paint | Architecture | II | 2023-10-06
Caulk Repair caulk | Architecture | Ghost Protocol | 2023-10-03
Punch List Recaulk Backsplash | Architecture | Ghost Protocol | 2023-10-08
Conduit too low Conduit coming from west corridor enters space and into Iso PreOp bathroom. Outside in alcove 1943A conduit is 7â€™-11â€ inside bathroom 8â€™ | Electrical | Fallout | 2023-10-05
Safety Bent/ warped beams one not secured on south side stair case on 3 needs fixed or replaced | Structural | I | 2023-10-07
Door G923F Inspection -- Hard Copy Included Fire Rated Opening - Inspection | Fire Protection | III | 2023-10-02
Punch List Install base | Architecture | Final Reckoning | 2023-10-04
HVAC VS Steel kicker Supply duct to re-route out of steel. (Steel has priority) | Mechanical | Rogue Nation | 2023-10-09
CCHMC Commissioning - Interior Power Duplex receptacle not installed per design. see a.ttached for receptacle labeled with "NI" | Electrical | I | 2023-10-10
Warranty Issue HVAC: Warehouse gas-fired heater is not part of current HVAC maintenance scope and should be considered to be added. | Mechanical | Final Reckoning | 2023-10-05
Install Silt Fencing Install correct type of silt fencing as specified in Civil Drawings at marked deficient location | Civil | Rogue Nation | 2023-10-04
Punch List 312 - clean | Architecture | Fallout | 2023-10-09
Drop diffusers Install diffusers | Mechanical | I | 2023-10-01
Safety There was one ground fault receptacle that the cover was falling off on the third floor. I spoke to an electrician and he repaired it | Electrical | I | 2023-10-08
Messer Punch List Drywall touch up and paint needed. Rm 2129 | Architecture | Dead Reckoning | 2023-10-03
SME Caulk temp holes | Architecture | Fallout | 2023-10-04
Paint Paint at base | Architecture | I | 2023-10-10
Quality Lights need aimed at artwork on east wall | Electrical | Dead Reckoning | 2023-10-02
Warranty By bulkhead, pinhole spot at wall/ceiling/bulkhead joint. | Architecture | Fallout | 2023-10-07
Run condensate lines separately Run condensate lines to drain from AHU-1 humidifier separately from AHU-1 coils | Mechanical | Ghost Protocol | 2023-10-07
Safety Straighten loose conduit and tool | Electrical | Rogue Nation | 2023-10-01
822 Pre-Final Punchlist - Messer Clean replace dirty pads above door | Architecture | III | 2023-10-03
Quality Need nurse call | Communications | II | 2023-10-10
Ceiling Tile Ceiling tile damaged/stained. | Architecture | Final Reckoning | 2023-10-03
Punch List walls need to be cleaned and touched up | Architecture | III | 2023-10-02
Set Wi-Fi fixture and sensor Set the Wi-Fi, router and sensor fixtures on to acoustical grid | Communications | Ghost Protocol | 2023-10-10
Remove paint on border Remove paint on border | Architecture | Fallout | 2023-10-03
Punch List Missing mortar at brick | Architecture | III | 2023-10-01
Automatic Flush Valves Install all flush valves to both toilets | Plumbing | Rogue Nation | 2023-10-06
Quality 4th floor riser piping for refrigerant and condensation system - no deficiencies found | Mechanical | I | 2023-10-10
Punch List Fix door trim | Architecture | Ghost Protocol | 2023-10-09
Pre-Punch List Fire caulk | Fire Protection | II | 2023-10-10
5S Organize Sheetrock pile | Architecture | Ghost Protocol | 2023-10-09
L3E: Label sprinkler Pipe at arrows Label | Fire Protection | Ghost Protocol | 2023-10-01
Above Ceiling Issue Complete top out and fire caulk top of wall | Fire Protection | I | 2023-10-10
Complete wall base installation. Complete wall base installation. | Architecture | Rogue Nation | 2023-10-09
Firestop penetration Fire stop electrical penetration | Fire Protection | Dead Reckoning | 2023-10-01
Quality Notch the corner better. Pipe canâ€™t be touching | Plumbing | Ghost Protocol | 2023-10-04
Punch List Fire proofing | Fire Protection | Ghost Protocol | 2023-10-08
Punch List Complete installation of ceiling panel | Architecture | Rogue Nation | 2023-10-05
Quality Rework panel joint for a consistent dimension | Architecture | III | 2023-10-04
Pre-Punch List Touch up drywall at diffuser. | Architecture | II | 2023-10-09
Paint Touch Up Repair messy corners at crown | Architecture | Ghost Protocol | 2023-10-04
F/A paint red Denier | Fire Protection | Rogue Nation | 2023-10-01
Punch List - 115 Mayers Complete device and cover plate install | Electrical | III | 2023-10-05
Seal backsplash at wall Seal backsplash at wall | Architecture | II | 2023-10-04
Punch List - 3rd Floor Unit E Column damaged and EIFs will need repaired unit e balcony | Structural | I | 2023-10-04
Touch Up Walls Touch Up Walls | Architecture | Rogue Nation | 2023-10-10
Punch List 3213 Dings scuff on walls | Architecture | Rogue Nation | 2023-10-03
Quality Missing corner guard, room 048 | Architecture | Ghost Protocol | 2023-10-05
Wall Paint Touch-Up Wall paint needs touch up. | Architecture | Rogue Nation | 2023-10-08
Owner/Arch Final Punch Leak in garage. Need to remove planter materials and waterproof. | Civil | Dead Reckoning | 2023-10-01
Safety Gfci should be plugged in closely to power source not used as a connector. Level 5 s w | Electrical | Dead Reckoning | 2023-10-09
Puncture hazard Point on end of demoed slab could puncture someone. Needs to be broken off. | Structural | Final Reckoning | 2023-10-01
Punch List Door doesnâ€™t close | Architecture | Fallout | 2023-10-05
Punch List Remove tie wire | Structural | Fallout | 2023-10-08
Punch List Finish painting East wall | Architecture | Ghost Protocol | 2023-10-01
Add stencil where fire caulk stops Add stencil where fire caulk starts/stops | Fire Protection | III | 2023-10-06
Safety - hanging conduit. Overhead hazard. Hanging conduit. Hanging all the way to floor. Need to tie up. Overhead safety. While itâ€™s not all the way down to the floor, it is still low enough to able to walk up and hit. | Electrical | Rogue Nation | 2023-10-03
Quality Fix caulk at interface between new and old buildings | Architecture | Dead Reckoning | 2023-10-03
Checklist Damage | no | Dead Reckoning | 2023-10-10
Blocking Missing casework blocking | Architecture | III | 2023-10-01
Pre-Punch List Tie in acid waste once eye wash is installed | Plumbing | III | 2023-10-05
Precast Panel #1022 (109) Chips along the bottom and top left edge | Architecture | II | 2023-10-10
Punch List Clean sill | Architecture | Dead Reckoning | 2023-10-01
Pre-Punch List bld draw 123 Floor clean Fire alarm box open | Fire Protection | Dead Reckoning | 2023-10-05
Exterior Punchlist - Enterprise Roofing Tower Roof - Remove roofing adhesive from metal panels at screen wall and elevator penthouse. (various locations) | Architecture | Dead Reckoning | 2023-10-02
Rebar and snow fencing Snow fencing and rebar are laying on the ground | Civil | Final Reckoning | 2023-10-03
Safety Heat detectors were lowered/relocated during demo and k13. Owner requires them to be secured up high in order to be effective. | Fire Protection | Fallout | 2023-10-04
Punch List 1140. Left door cylinder loose | Architecture | II | 2023-10-01
Above Ceiling Issue Provide proper j hooks on existing cables | Communications | Final Reckoning | 2023-10-03